## Tabel 1 Adresgegevens
Tabel 1 - Adresgegevens
Informatieverzoek van ACM/Directie Energie in het kader van CODATA
Onderwerp | NorNed bonus/malus
Referentiejaar | 2018
DOX-nummer | ACM/18/034530
Datum ingevuld | 2019-01-30
Adresgegevens
Naam bedrijf | TenneT TSO B.V.
Adres | Postbus 718
Postcode | 6800 AS
Plaats | Arnhem
Contactgegevens ACM ten behoeve van deze uitvraag
Postbus 16326
2500 BH DEN HAAG
tel : 070 - 722 2194
e-mail : CODATA_Netbeheerders@acm.nl

## Tabel 2 Berekening bonus-malus
Tabel 2 - Berekening bonus/malus
Beschrijving resultaat
Op dit tabblad berekent de ACM de bonus/malus (het prikkelbedrag) voor de relatieve beschikbaarheid van de NorNed-kabel in 2018. TenneT mag dit bedrag in het boekjaar 2019 met de veilinggelden verrekenen.
Omschrijving | Eenheid | Constante | Bron | Hyperlink | Opmerking
Ophalen gegevens voor berekening
CPI
CPI 2005 | % | 1.1% | CBS Statline |  | De relatieve wijziging van de consumentenprijsindex wordt berekend uit het quotiënt van deze index, gepubliceerd in de vierde maand voorafgaande aan het jaar t, en van deze index, gepubliceerd
CPI 2006 | % | 1.8% | CBS Statline |  | in de zestiende maand voorafgaande aan het jaar t, zoals deze maandelijks wordt vastgesteld door het CBS.
CPI 2007 | % | 1.4% | CBS Statline |  | De gegevens zijn afkomstig uit StatLine, zie voor recente CPI-cijfers: https://opendata.cbs.nl/statline/#/CBS/nl/dataset/70936ned/table?ts=1532343719053.
CPI 2008 | % | 1.1% | CBS Statline
CPI 2009 | % | 3.2% | CBS Statline
CPI 2010 | % | 0.3% | CBS Statline
CPI 2011 | % | 1.5% | CBS Statline
CPI 2012 | % | 2.6% | CBS Statline
CPI 2013 | % | 2.3% | CBS Statline
CPI 2014 | % | 2.8% | CBS Statline
CPI 2015 | % | 1% | CBS Statline
CPI 2016 | % | 0.8% | CBS Statline
CPI 2017 | % | 0.2% | CBS Statline
CPI 2018 | % | 1.4% | CBS Statline
Bonus/malus
Bonus/malus per 1% beschikbaarheid boven norm | EUR | 400000 | NorNed-besluit, bijlage A, rn. 16 | hier
Maximum bonus/malus | EUR | 1200000 | NorNed-besluit, bijlage A, rn. 16 | hier
Capaciteit
Capaciteit NorNed exclusief netverliezen | MW | 700
Capaciteit NorNed inclusief netverliezen | MW | 723
Multiplier netverliezen |  | 1.0329 |  |  | Dit getal wordt gebruikt om in kolom M van Tabel 3 de beschikbare capaciteit inclusief netverliezen om te zetten naar de beschikbare capaciteit exclusief netverliezen.
Nominale capaciteit | MW | 683.86 | Vaststelling nominale capaciteit NorNed-kabel, rn. 34 | hier
Norm relatieve beschikbaarheid | % | 95.62% | NorNed-besluit, bijlage A, rn. 16 | hier
Restricties
Totaal DA-restricties | MW | 1324632
Beperkingen force majeure | MW | 0
Beperkingen Noorse AC net | MW | 262002
Restrictie TenneT excl. intraday | MW | 1062630
Restrictie TenneT incl. intraday | MW | 1036906
Correcties | MW | 16902
Uren
Totaal aantal uren in 2018 | uren | 8760
Berekening bonus/malus
Beperkingen door TenneT | MW | 1020004
Beschikbaar gestelde capaciteit in 2018 | MW | 5111996
Nominale capaciteit in 2018 | MW | 5990613.6
Relatieve beschikbaarheid | % | 85.33%
Verschil tussen relatieve beschikbaarheid en norm | %-punt | -10.2866
Bonus/malus | EUR | -4114628.4202
Inflatie van 2004 naar 2018 | 1+% | 1.2372
Bonus/malus inclusief inflatiecorrectie | EUR | -1484634.8619

## Tabel 3 Beschikbaarheid NorNed
Tabel 3 - Beschikbaarheid NorNed |  |  |  |  | day ahead |  |  | intraday |  |  |  | restrictie |  |  |  | day ahead flow |  |  | intraday flow
Dag | uren | force majeure: j/n | Noorse AC net restrictie: j/n | hyperlink naar UMM | NO2 > NL | NL > NO2 | totaal | NO2 > NL | NL > NO2 | totaal | . | totaal DA op NorNed | TenneT incl. intraday | TenneT excl. intraday | . | NO2 > NL | NL > NO2 | . | NO2 > NL | NL > NO2 | . | corr TenneT j/n | corr. Beschibaarheid (MW) | Toelichting TenneT
2018-01-01 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 586 | 814 | 1400 |  | 0 | 0 | 0 |  | 117.6 | 0 |  | 0 | 148 |  | n | 0
2018-01-01 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 154 | 1246 | 1400 |  | 0 | 0 | 0 |  | 563.5 | 0 |  | 0 | 467.3 |  | n | 0
2018-01-01 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 382 | 1018 | 1400 |  | 0 | 0 | 0 |  | 328.5 | 0 |  | 0 | 471 |  | n | 0
2018-01-01 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 981 | 419 | 1400 |  | 0 | 0 | 0 |  | 0 | 290.5 |  | 0 | 351.6 |  | n | 0
2018-01-01 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 610 | 790 | 1400 |  | 0 | 0 | 0 |  | 93.2 | 0 |  | 0 | 315 |  | n | 0
2018-01-01 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 696 | 704 | 1400 |  | 0 | 0 | 0 |  | 4.3 | 0 |  | 0 | 309.7 |  | n | 0
2018-01-01 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 586 | 814 | 1400 |  | 0 | 0 | 0 |  | 117.6 | 0 |  | 0 | 269 |  | n | 0
2018-01-01 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 393.7 |  | n | 0
2018-01-01 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 338 | 1062 | 1400 |  | 0 | 0 | 0 |  | 374.3 | 0 |  | 0 | 631.1 |  | n | 0
2018-01-01 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 351 | 1049 | 1400 |  | 0 | 0 | 0 |  | 360.9 | 0 |  | 0 | 610.6 |  | n | 0
2018-01-01 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 469 |  | n | 0
2018-01-01 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 290.1 |  | n | 0
2018-01-01 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 123.5 |  | n | 0
2018-01-01 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 50 |  | n | 0
2018-01-01 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 102 |  | n | 0
2018-01-01 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-01 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-01 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-01 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-01 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-01 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-01 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 76 | 1324 | 1400 |  | 0 | 0 | 0 |  | 644.2 | 0 |  | 46 | 0 |  | n | 0
2018-01-01 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 553 | 847 | 1400 |  | 0 | 0 | 0 |  | 151.5 | 0 |  | 0 | 0 |  | n | 0
2018-01-01 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 1153 | 247 | 1400 |  | 0 | 0 | 0 |  | 0 | 467.5 |  | 0 | 0 |  | n | 0
2018-01-02 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 853 | 147 | 1000 |  | 401 | 401 | 401 |  | 0 | 571.2 |  | 0 | 147 |  | n | 0 | Outage
2018-01-02 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1000 | 0 | 1000 |  | 401 | 401 | 401 |  | 0 | 723 |  | 0 | 0 |  | n | 0 | Outage
2018-01-02 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 497 | 503 | 1000 |  | 401 | 401 | 401 |  | 0 | 203 |  | 0 | 171.5 |  | n | 0 | Outage
2018-01-02 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 700 | 300 | 1000 |  | 401 | 401 | 401 |  | 0 | 413.3 |  | 0 | 173.6 |  | n | 0 | Outage
2018-01-02 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 857 | 143 | 1000 |  | 401 | 401 | 401 |  | 0 | 575.9 |  | 0 | 28.4 |  | n | 0 | Outage
2018-01-02 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 732 | 268 | 1000 |  | 401 | 401 | 401 |  | 0 | 445.9 |  | 0 | 268 |  | n | 0 | Outage
2018-01-02 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 600 | 400 | 1000 |  | 401 | 401 | 401 |  | 0 | 310 |  | 0 | 0 |  | n | 0 | Outage
2018-01-02 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1 | 999 | 1000 |  | 401 | 401 | 401 |  | 309 | 0 |  | 1 | 0 |  | n | 0 | Outage
2018-01-02 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 600 | 400 | 1000 |  | 401 | 401 | 401 |  | 0 | 310 |  | 0 | 0 |  | n | 0 | Outage
2018-01-02 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 634 | 366 | 1000 |  | 401 | 401 | 401 |  | 0 | 345.2 |  | 350.7 | 0 |  | j | 401 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-02 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 98 | 902 | 1000 |  | 401 | 401 | 401 |  | 209 | 0 |  | 270.2 | 0 |  | j | 401 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 657 | 743 | 1400 |  | 401 | 0 | 401 |  | 44.9 | 0 |  | 0 | 7.1 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 800 | 600 | 1400 |  | 401 | 0 | 401 |  | 0 | 143.7 |  | 24.8 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1400 | 0 | 1400 |  | 401 | 0 | 401 |  | 0 | 723 |  | 0 | 14.2 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1400 | 0 | 1400 |  | 401 | 0 | 401 |  | 0 | 723 |  | 0 | 19 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 1359 | 41 | 1400 |  | 401 | 0 | 401 |  | 0 | 680.2 |  | 59.4 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 864 | 536 | 1400 |  | 401 | 0 | 401 |  | 0 | 221.2 |  | 93.5 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 596 | 804 | 1400 |  | 401 | 0 | 401 |  | 107.2 | 0 |  | 132 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 437.6 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 700 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 364 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 230 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 20 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-03 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/33f0da88-6a25-4c97-8963-0bf6f526dba3/3 | 309 | 723 | 1032 | 401 | 999 | 1400 |  | 401 | 0 | 401 |  | 309 | 0 |  | 228.5 | 0 |  | j | 0 | Initially not available until 03/01/2018 23:59 (UMM 02/01/2018 07:33). Subsequently event stop updated to 02/01/2018 17:32 (UMM 02/01/2018 17:49). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-01-04 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 53 | 1347 | 1400 |  | 0 | 0 | 0 |  | 668.8 | 0 |  | 0 | 181 |  | n | 0
2018-01-04 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 586 | 814 | 1400 |  | 0 | 0 | 0 |  | 118.2 | 0 |  | 0 | 111 |  | n | 0
2018-01-04 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 108 | 1292 | 1400 |  | 0 | 0 | 0 |  | 611.1 | 0 |  | 0 | 104 |  | n | 0
2018-01-04 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 15 |  | n | 0
2018-01-04 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 25 |  | n | 0
2018-01-04 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 20 |  | n | 0
2018-01-04 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-04 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 75 |  | n | 0
2018-01-05 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 1199 | 201 | 1400 |  | 0 | 0 | 0 |  | 0 | 515 |  | 0 | 0 |  | n | 0
2018-01-05 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-05 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-05 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 801 | 599 | 1400 |  | 0 | 0 | 0 |  | 0 | 104 |  | 0 | 0 |  | n | 0
2018-01-05 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 846 | 554 | 1400 |  | 0 | 0 | 0 |  | 0 | 151.2 |  | 54.1 | 0 |  | n | 0
2018-01-05 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 583 | 817 | 1400 |  | 0 | 0 | 0 |  | 120.8 | 0 |  | 0 | 12 |  | n | 0
2018-01-05 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-05 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 128.2 | 0 |  | n | 0
2018-01-06 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 107.9 | 0 |  | n | 0
2018-01-06 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 10 | 0 |  | n | 0
2018-01-06 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 151 | 1249 | 1400 |  | 0 | 0 | 0 |  | 567.4 | 0 |  | 0 | 21.7 |  | n | 0
2018-01-06 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 126 | 1274 | 1400 |  | 0 | 0 | 0 |  | 592.7 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 255.5 | 0 |  | n | 0
2018-01-06 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 484 | 916 | 1400 |  | 0 | 0 | 0 |  | 222.9 | 0 |  | 96.2 | 0 |  | n | 0
2018-01-06 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-06 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 0 |  | n | 0
2018-01-07 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 1199 | 201 | 1400 |  | 0 | 0 | 0 |  | 0 | 515 |  | 0 | 0 |  | n | 0
2018-01-07 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-07 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-07 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-07 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-07 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-07 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-07 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-07 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 1387 | 13 | 1400 |  | 0 | 0 | 0 |  | 0 | 709.3 |  | 0 | 13 |  | n | 0
2018-01-07 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 787 | 613 | 1400 |  | 0 | 0 | 0 |  | 0 | 90.3 |  | 0 | 155.2 |  | n | 0
2018-01-07 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 352 | 1048 | 1400 |  | 0 | 0 | 0 |  | 359.6 | 0 |  | 0 | 87.7 |  | n | 0
2018-01-07 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 423 | 977 | 1400 |  | 0 | 0 | 0 |  | 285.8 | 0 |  | 0 | 12.7 |  | n | 0
2018-01-07 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 392 | 1008 | 1400 |  | 0 | 0 | 0 |  | 317.9 | 0 |  | 0 | 44 |  | n | 0
2018-01-07 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 395 | 1005 | 1400 |  | 0 | 0 | 0 |  | 314.7 | 0 |  | 0 | 155 |  | n | 0
2018-01-07 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 151 | 1249 | 1400 |  | 0 | 0 | 0 |  | 566.6 | 0 |  | 0 | 301.8 |  | n | 0
2018-01-07 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 67 | 1333 | 1400 |  | 0 | 0 | 0 |  | 653.5 | 0 |  | 0 | 199.8 |  | n | 0
2018-01-07 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 178.2 |  | n | 0
2018-01-07 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 88.9 |  | n | 0
2018-01-07 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-07 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-07 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 101 | 1299 | 1400 |  | 0 | 0 | 0 |  | 619 | 0 |  | 101 | 0 |  | n | 0
2018-01-07 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 700 | 0 |  | n | 0
2018-01-07 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 601 | 0 |  | n | 0
2018-01-07 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 1 | 0 |  | n | 0
2018-01-08 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 1299 | 101 | 1400 |  | 0 | 0 | 0 |  | 0 | 619 |  | 0 | 0 |  | n | 0
2018-01-08 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-08 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-08 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-08 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-08 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 1299 | 101 | 1400 |  | 0 | 0 | 0 |  | 0 | 619 |  | 0 | 1 |  | n | 0
2018-01-08 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 101 | 1299 | 1400 |  | 0 | 0 | 0 |  | 619 | 0 |  | 1 | 0 |  | n | 0
2018-01-08 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-08 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 85 |  | n | 0
2018-01-09 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 20 |  | n | 0
2018-01-09 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-09 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-10 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-10 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-10 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 117 | 1283 | 1400 |  | 0 | 0 | 0 |  | 602.3 | 0 |  | 117 | 0 |  | n | 0
2018-01-10 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 349 | 1051 | 1400 |  | 0 | 0 | 0 |  | 362.2 | 0 |  | 0 | 24.4 |  | n | 0
2018-01-10 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-10 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 301 | 1099 | 1400 |  | 0 | 0 | 0 |  | 412.2 | 0 |  | 144.6 | 0 |  | n | 0
2018-01-10 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-10 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 395.4 | 0 |  | n | 0
2018-01-10 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 484 | 916 | 1400 |  | 0 | 0 | 0 |  | 223.5 | 0 |  | 484 | 0 |  | n | 0
2018-01-10 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 47 | 1353 | 1400 |  | 0 | 0 | 0 |  | 674.7 | 0 |  | 47 | 0 |  | n | 0
2018-01-10 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 85 | 1315 | 1400 |  | 0 | 0 | 0 |  | 635.6 | 0 |  | 85 | 0 |  | n | 0
2018-01-10 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-10 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-10 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 353 | 1047 | 1400 |  | 0 | 0 | 0 |  | 358.3 | 0 |  | 353 | 0 |  | n | 0
2018-01-10 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 478 | 922 | 1400 |  | 0 | 0 | 0 |  | 229.2 | 0 |  | 478 | 0 |  | n | 0
2018-01-10 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 577 | 823 | 1400 |  | 0 | 0 | 0 |  | 126.9 | 0 |  | 212 | 0 |  | n | 0
2018-01-10 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-01-10 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 77 | 0 |  | n | 0
2018-01-10 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 520 | 880 | 1400 |  | 0 | 0 | 0 |  | 185.4 | 0 |  | 150 | 0 |  | n | 0
2018-01-10 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-10 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 10 |  | n | 0
2018-01-10 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 298 | 1102 | 1400 |  | 0 | 0 | 0 |  | 415.8 | 0 |  | 112.7 | 0 |  | n | 0
2018-01-10 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-10 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 528 | 872 | 1400 |  | 0 | 0 | 0 |  | 177.5 | 0 |  | 0.5 | 0 |  | n | 0
2018-01-11 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 66 | 1334 | 1400 |  | 0 | 0 | 0 |  | 655 | 0 |  | 66 | 0 |  | n | 0
2018-01-11 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 404 | 996 | 1400 |  | 0 | 0 | 0 |  | 306.1 | 0 |  | 40 | 0 |  | n | 0
2018-01-11 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 630 | 770 | 1400 |  | 0 | 0 | 0 |  | 72.7 | 0 |  | 0 | 23.3 |  | n | 0
2018-01-11 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 173 | 1227 | 1400 |  | 0 | 0 | 0 |  | 544 | 0 |  | 0 | 20 |  | n | 0
2018-01-11 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-11 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0.1 |  | n | 0
2018-01-12 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 70.8 |  | n | 0
2018-01-12 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-12 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-13 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 101 | 1299 | 1400 |  | 0 | 0 | 0 |  | 619 | 0 |  | 101 | 0 |  | n | 0
2018-01-14 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 189.5 | 0 |  | n | 0
2018-01-14 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 691 | 709 | 1400 |  | 0 | 0 | 0 |  | 9.3 | 0 |  | 384.1 | 0 |  | n | 0
2018-01-14 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 92 | 1308 | 1400 |  | 0 | 0 | 0 |  | 628.3 | 0 |  | 92 | 0 |  | n | 0
2018-01-14 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-14 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 35 |  | n | 0
2018-01-15 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 31 | 1369 | 1400 |  | 0 | 0 | 0 |  | 691.2 | 0 |  | 31 | 0 |  | n | 0
2018-01-15 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 66 | 1334 | 1400 |  | 0 | 0 | 0 |  | 655 | 0 |  | 0.2 | 0 |  | n | 0
2018-01-15 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 90 | 1310 | 1400 |  | 0 | 0 | 0 |  | 629.8 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 10 |  | n | 0
2018-01-15 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-15 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 20 |  | n | 0
2018-01-16 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 100.4 |  | n | 0
2018-01-16 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 71.4 |  | n | 0
2018-01-16 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 664 | 736 | 1400 |  | 0 | 0 | 0 |  | 36.7 | 0 |  | 0 | 50 |  | n | 0
2018-01-16 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 304 | 1096 | 1400 |  | 0 | 0 | 0 |  | 409 | 0 |  | 0 | 45 |  | n | 0
2018-01-16 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-16 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 618.9 | 0 |  | 69.8 | 0 |  | n | 0
2018-01-17 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 215.7 | 0 |  | 0 | 140.2 |  | n | 0
2018-01-17 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 403.3 |  | 0 | 91.2 |  | n | 0
2018-01-17 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 598 |  | 0 | 23.8 |  | n | 0
2018-01-17 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 200.2 |  | 76 | 0 |  | n | 0
2018-01-17 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 418.8 | 0 |  | 70 | 0 |  | n | 0
2018-01-17 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 50.1 |  | n | 0
2018-01-17 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-17 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 20 |  | n | 0
2018-01-18 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 310 | 1090 | 1400 |  | 0 | 0 | 0 |  | 403.2 | 0 |  | 0 | 27 |  | n | 0
2018-01-18 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 294 | 1106 | 1400 |  | 0 | 0 | 0 |  | 419 | 0 |  | 0 | 60 |  | n | 0
2018-01-18 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 894 | 506 | 1400 |  | 0 | 0 | 0 |  | 0 | 200 |  | 0 | 60 |  | n | 0
2018-01-18 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-18 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-18 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 801 | 599 | 1400 |  | 0 | 0 | 0 |  | 0 | 104 |  | 1 | 0 |  | n | 0
2018-01-18 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 260 | 1140 | 1400 |  | 0 | 0 | 0 |  | 454.1 | 0 |  | 60 | 0 |  | n | 0
2018-01-18 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 247 | 1153 | 1400 |  | 0 | 0 | 0 |  | 468.1 | 0 |  | 168.2 | 0 |  | n | 0
2018-01-18 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 323 | 1077 | 1400 |  | 0 | 0 | 0 |  | 389.5 | 0 |  | 0 | 17.6 |  | n | 0
2018-01-18 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-18 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-19 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-19 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 106 | 1294 | 1400 |  | 0 | 0 | 0 |  | 613.5 | 0 |  | 6 | 0 |  | n | 0
2018-01-19 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 50 | 0 |  | n | 0
2018-01-19 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-01-19 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 20 | 0 |  | n | 0
2018-01-19 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 30 | 0 |  | n | 0
2018-01-19 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 260 | 1140 | 1400 |  | 0 | 0 | 0 |  | 454.3 | 0 |  | 125 | 0 |  | n | 0
2018-01-19 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-01-19 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 64.1 | 0 |  | n | 0
2018-01-19 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 457 | 943 | 1400 |  | 0 | 0 | 0 |  | 251.1 | 0 |  | 66 | 0 |  | n | 0
2018-01-19 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 441 | 959 | 1400 |  | 0 | 0 | 0 |  | 267.1 | 0 |  | 163 | 0 |  | n | 0
2018-01-19 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 91 | 1309 | 1400 |  | 0 | 0 | 0 |  | 628.9 | 0 |  | 91 | 0 |  | n | 0
2018-01-19 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 403 | 997 | 1400 |  | 0 | 0 | 0 |  | 306.7 | 0 |  | 163 | 0 |  | n | 0
2018-01-19 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 76 | 0 |  | n | 0
2018-01-19 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-01-19 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 408 | 992 | 1400 |  | 0 | 0 | 0 |  | 302 | 0 |  | 81 | 0 |  | n | 0
2018-01-19 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 654 | 746 | 1400 |  | 0 | 0 | 0 |  | 47.4 | 0 |  | 81 | 0 |  | n | 0
2018-01-19 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 594 | 806 | 1400 |  | 0 | 0 | 0 |  | 109.1 | 0 |  | 51 | 0 |  | n | 0
2018-01-19 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 325 | 1075 | 1400 |  | 0 | 0 | 0 |  | 387.1 | 0 |  | 0 | 25 |  | n | 0
2018-01-19 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-19 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 189 | 1211 | 1400 |  | 0 | 0 | 0 |  | 527.8 | 0 |  | 189 | 0 |  | n | 0
2018-01-19 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-19 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-19 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 324 | 1076 | 1400 |  | 0 | 0 | 0 |  | 388.5 | 0 |  | 80 | 0 |  | n | 0
2018-01-20 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 515 | 885 | 1400 |  | 0 | 0 | 0 |  | 191.2 | 0 |  | 25 | 0 |  | n | 0
2018-01-20 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 378 | 1022 | 1400 |  | 0 | 0 | 0 |  | 332.1 | 0 |  | 23 | 0 |  | n | 0
2018-01-20 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 224 | 1176 | 1400 |  | 0 | 0 | 0 |  | 491.6 | 0 |  | 95 | 0 |  | n | 0
2018-01-20 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-20 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 442 | 958 | 1400 |  | 0 | 0 | 0 |  | 266.3 | 0 |  | 145 | 0 |  | n | 0
2018-01-21 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 238 | 0 |  | n | 0
2018-01-21 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 97.4 |  | n | 0
2018-01-21 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 574 | 826 | 1400 |  | 0 | 0 | 0 |  | 129.7 | 0 |  | 0 | 18.8 |  | n | 0
2018-01-21 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 1 | 0 |  | n | 0
2018-01-21 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 876 | 524 | 1400 |  | 0 | 0 | 0 |  | 0 | 181.8 |  | 0 | 0 |  | n | 0
2018-01-21 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 277 | 1123 | 1400 |  | 0 | 0 | 0 |  | 437.2 | 0 |  | 1 | 0 |  | n | 0
2018-01-21 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 214 | 1186 | 1400 |  | 0 | 0 | 0 |  | 502.1 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-21 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 80 |  | n | 0
2018-01-21 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 247.1 |  | n | 0
2018-01-22 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 248.1 |  | n | 0
2018-01-22 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 1199 | 201 | 1400 |  | 0 | 0 | 0 |  | 0 | 515 |  | 0 | 197 |  | n | 0
2018-01-22 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-22 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-22 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-22 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 889 | 511 | 1400 |  | 0 | 0 | 0 |  | 0 | 195.1 |  | 0 | 1 |  | n | 0
2018-01-22 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 290 | 1110 | 1400 |  | 0 | 0 | 0 |  | 423.9 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 239 | 1161 | 1400 |  | 0 | 0 | 0 |  | 476.5 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 444 | 956 | 1400 |  | 0 | 0 | 0 |  | 264.9 | 0 |  | 1.4 | 0 |  | n | 0
2018-01-22 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 272 | 1128 | 1400 |  | 0 | 0 | 0 |  | 441.9 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 624 | 776 | 1400 |  | 0 | 0 | 0 |  | 78.1 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 386 | 1014 | 1400 |  | 0 | 0 | 0 |  | 324.3 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 479 | 921 | 1400 |  | 0 | 0 | 0 |  | 228.4 | 0 |  | 137.4 | 0 |  | n | 0
2018-01-22 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 589 | 811 | 1400 |  | 0 | 0 | 0 |  | 115 | 0 |  | 28 | 0 |  | n | 0
2018-01-22 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 422 | 978 | 1400 |  | 0 | 0 | 0 |  | 286.6 | 0 |  | 38 | 0 |  | n | 0
2018-01-22 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 636 | 764 | 1400 |  | 0 | 0 | 0 |  | 65.7 | 0 |  | 93 | 0 |  | n | 0
2018-01-22 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 651 | 749 | 1400 |  | 0 | 0 | 0 |  | 50.4 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 309 | 1091 | 1400 |  | 0 | 0 | 0 |  | 403.8 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 196 | 1204 | 1400 |  | 0 | 0 | 0 |  | 520.9 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 722.6 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-22 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 387 | 1013 | 1400 |  | 0 | 0 | 0 |  | 323.1 | 0 |  | 8 | 0 |  | n | 0
2018-01-23 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 61 | 0 |  | n | 0
2018-01-23 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 41.6 |  | n | 0
2018-01-23 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 15.9 |  | n | 0
2018-01-23 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 340 | 1060 | 1400 |  | 0 | 0 | 0 |  | 372.1 | 0 |  | 0 | 20 |  | n | 0
2018-01-23 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 82 | 1318 | 1400 |  | 0 | 0 | 0 |  | 638.1 | 0 |  | 75 | 0 |  | n | 0
2018-01-23 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-23 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 348 | 1052 | 1400 |  | 0 | 0 | 0 |  | 363.7 | 0 |  | 0 | 94 |  | n | 0
2018-01-24 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 372 | 1028 | 1400 |  | 0 | 0 | 0 |  | 338.4 | 0 |  | 0 | 174 |  | n | 0
2018-01-24 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 613 | 787 | 1400 |  | 0 | 0 | 0 |  | 90.1 | 0 |  | 0 | 299.5 |  | n | 0
2018-01-24 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 911 | 489 | 1400 |  | 0 | 0 | 0 |  | 0 | 218.2 |  | 0 | 253.5 |  | n | 0
2018-01-24 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 974 | 426 | 1400 |  | 0 | 0 | 0 |  | 0 | 283.5 |  | 0 | 275.4 |  | n | 0
2018-01-24 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 997 | 403 | 1400 |  | 0 | 0 | 0 |  | 0 | 306.4 |  | 57 | 0 |  | n | 0
2018-01-24 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 510 | 890 | 1400 |  | 0 | 0 | 0 |  | 196.2 | 0 |  | 170 | 0 |  | n | 0
2018-01-24 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-24 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 720.8 | 0 |  | 2 | 0 |  | n | 0
2018-01-25 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 511 | 889 | 1400 |  | 0 | 0 | 0 |  | 195.1 | 0 |  | 48 | 0 |  | n | 0
2018-01-25 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 911 | 489 | 1400 |  | 0 | 0 | 0 |  | 0 | 217.4 |  | 138.6 | 0 |  | n | 0
2018-01-25 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 1220 | 180 | 1400 |  | 0 | 0 | 0 |  | 0 | 537.5 |  | 118.3 | 0 |  | n | 0
2018-01-25 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 1199 | 201 | 1400 |  | 0 | 0 | 0 |  | 0 | 515 |  | 69 | 0 |  | n | 0
2018-01-25 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 69 | 0 |  | n | 0
2018-01-25 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-25 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-26 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 116 | 1284 | 1400 |  | 0 | 0 | 0 |  | 603.4 | 0 |  | 20 | 0 |  | n | 0
2018-01-27 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 10 | 1390 | 1400 |  | 0 | 0 | 0 |  | 713.2 | 0 |  | 10 | 0 |  | n | 0
2018-01-27 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 533 | 867 | 1400 |  | 0 | 0 | 0 |  | 172.8 | 0 |  | 533 | 0 |  | n | 0
2018-01-27 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 599 | 0 |  | n | 0
2018-01-27 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-27 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 96.5 |  | n | 0
2018-01-28 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 120.9 |  | n | 0
2018-01-28 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 122 | 1278 | 1400 |  | 0 | 0 | 0 |  | 596.9 | 0 |  | 0 | 262.6 |  | n | 0
2018-01-28 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 602 | 798 | 1400 |  | 0 | 0 | 0 |  | 101 | 0 |  | 0 | 94.9 |  | n | 0
2018-01-28 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 3 | 1397 | 1400 |  | 0 | 0 | 0 |  | 720 | 0 |  | 0 | 242.4 |  | n | 0
2018-01-28 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 375 | 1025 | 1400 |  | 0 | 0 | 0 |  | 335.4 | 0 |  | 0 | 350.4 |  | n | 0
2018-01-28 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 266.6 |  | n | 0
2018-01-28 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 250.2 |  | n | 0
2018-01-28 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 305.8 |  | n | 0
2018-01-28 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 185 |  | n | 0
2018-01-28 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-28 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-28 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-28 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 21.2 |  | n | 0
2018-01-28 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 32 |  | n | 0
2018-01-28 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 55.5 |  | n | 0
2018-01-28 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 24 |  | n | 0
2018-01-28 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 107 |  | n | 0
2018-01-28 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 9.4 |  | n | 0
2018-01-28 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-28 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 39.2 |  | n | 0
2018-01-28 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 104.5 |  | n | 0
2018-01-28 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 98.3 |  | n | 0
2018-01-28 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 112 |  | n | 0
2018-01-28 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 409.4 |  | n | 0
2018-01-29 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 440 | 960 | 1400 |  | 0 | 0 | 0 |  | 318.5 | 0 |  | 0 | 153 |  | n | 0
2018-01-29 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 771 | 629 | 1400 |  | 0 | 0 | 0 |  | 0 | 73.7 |  | 0 | 143.5 |  | n | 0
2018-01-29 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 1371 | 29 | 1400 |  | 0 | 0 | 0 |  | 0 | 692.7 |  | 0 | 29 |  | n | 0
2018-01-29 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-29 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-01-29 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 1200 | 200 | 1400 |  | 0 | 0 | 0 |  | 0 | 515.9 |  | 0 | 1 |  | n | 0
2018-01-29 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 600 | 800 | 1400 |  | 0 | 0 | 0 |  | 103.1 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 1 | 1399 | 1400 |  | 0 | 0 | 0 |  | 722.1 | 0 |  | 1 | 0 |  | n | 0
2018-01-29 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-29 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-30 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 4 | 1396 | 1400 |  | 0 | 0 | 0 |  | 718.5 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 604 | 796 | 1400 |  | 0 | 0 | 0 |  | 99.5 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 902 | 498 | 1400 |  | 0 | 0 | 0 |  | 0 | 208.9 |  | 0 | 302 |  | n | 0
2018-01-31 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 892 | 508 | 1400 |  | 0 | 0 | 0 |  | 0 | 198.4 |  | 0 | 474.7 |  | n | 0
2018-01-31 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 826 | 574 | 1400 |  | 0 | 0 | 0 |  | 0 | 129.8 |  | 0 | 3.7 |  | n | 0
2018-01-31 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 226 | 1174 | 1400 |  | 0 | 0 | 0 |  | 489.2 | 0 |  | 0 | 23.7 |  | n | 0
2018-01-31 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-01-31 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 11 | 1389 | 1400 |  | 0 | 0 | 0 |  | 711.5 | 0 |  | 11 | 0 |  | n | 0
2018-02-01 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 30 | 1370 | 1400 |  | 0 | 0 | 0 |  | 691.8 | 0 |  | 30 | 0 |  | n | 0
2018-02-01 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 606 | 794 | 1400 |  | 0 | 0 | 0 |  | 97.4 | 0 |  | 293.9 | 0 |  | n | 0
2018-02-01 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 820 | 580 | 1400 |  | 0 | 0 | 0 |  | 0 | 123.4 |  | 447.8 | 0 |  | n | 0
2018-02-01 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 403 | 997 | 1400 |  | 0 | 0 | 0 |  | 306.7 | 0 |  | 403 | 0 |  | n | 0
2018-02-01 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 2.2 |  | n | 0
2018-02-01 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-01 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 101 | 1299 | 1400 |  | 0 | 0 | 0 |  | 619 | 0 |  | 101 | 0 |  | n | 0
2018-02-02 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 310.7 | 0 |  | n | 0
2018-02-02 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 700 | 0 |  | n | 0
2018-02-02 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 337 | 1063 | 1400 |  | 0 | 0 | 0 |  | 374.8 | 0 |  | 337 | 0 |  | n | 0
2018-02-02 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 265.4 | 0 |  | n | 0
2018-02-02 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 599 | 0 |  | n | 0
2018-02-02 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-02 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-03 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 581.2 | 0 |  | n | 0
2018-02-04 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 539.6 | 0 |  | n | 0
2018-02-04 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 384 | 1016 | 1400 |  | 0 | 0 | 0 |  | 326 | 0 |  | 309.2 | 0 |  | n | 0
2018-02-04 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 345 | 1055 | 1400 |  | 0 | 0 | 0 |  | 366.2 | 0 |  | 224 | 0 |  | n | 0
2018-02-04 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 50 | 0 |  | n | 0
2018-02-04 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-04 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-05 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 239 | 1161 | 1400 |  | 0 | 0 | 0 |  | 476.2 | 0 |  | 25.1 | 0 |  | n | 0
2018-02-05 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 19 | 1381 | 1400 |  | 0 | 0 | 0 |  | 703.7 | 0 |  | 0 | 0 |  | n | 0
2018-02-05 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 618 | 782 | 1400 |  | 0 | 0 | 0 |  | 84.7 | 0 |  | 0 | 1 |  | n | 0
2018-02-05 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-02-05 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 96.6 |  | n | 0
2018-02-05 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 14.4 | 0 |  | n | 0
2018-02-05 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 101 | 1299 | 1400 |  | 0 | 0 | 0 |  | 619 | 0 |  | 1.1 | 0 |  | n | 0
2018-02-05 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0.1 | 0 |  | n | 0
2018-02-05 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 5.3 |  | n | 0
2018-02-05 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 2.4 |  | n | 0
2018-02-05 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 794 | 606 | 1400 |  | 0 | 0 | 0 |  | 0 | 97.1 |  | 90 | 0 |  | n | 0
2018-02-05 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 789 | 611 | 1400 |  | 0 | 0 | 0 |  | 0 | 92.1 |  | 0 | 71.6 |  | n | 0
2018-02-05 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 269.7 | 0 |  | n | 0
2018-02-05 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 111 | 0 |  | n | 0
2018-02-05 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 239.6 | 0 |  | n | 0
2018-02-05 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 315 | 1085 | 1400 |  | 0 | 0 | 0 |  | 397.2 | 0 |  | 197.9 | 0 |  | n | 0
2018-02-05 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 652 | 748 | 1400 |  | 0 | 0 | 0 |  | 49.8 | 0 |  | 0 | 25 |  | n | 0
2018-02-05 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 235 |  | n | 0
2018-02-05 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 220 |  | n | 0
2018-02-05 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 35 |  | n | 0
2018-02-05 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 19.9 |  | n | 0
2018-02-05 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 49.9 | 0 |  | n | 0
2018-02-05 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 15 |  | n | 0
2018-02-05 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 457 | 943 | 1400 |  | 0 | 0 | 0 |  | 251.3 | 0 |  | 100.8 | 0 |  | n | 0
2018-02-06 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 134.2 | 0 |  | n | 0
2018-02-06 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 141 | 0 |  | n | 0
2018-02-06 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 45.6 | 0 |  | n | 0
2018-02-06 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 228.9 | 0 |  | n | 0
2018-02-06 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 50.3 | 0 |  | n | 0
2018-02-06 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 91.7 | 0 |  | n | 0
2018-02-06 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-02-06 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 806 | 594 | 1400 |  | 0 | 0 | 0 |  | 0 | 109.5 |  | 0 | 0 |  | n | 0
2018-02-06 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 1088 | 312 | 1400 |  | 0 | 0 | 0 |  | 0 | 400.5 |  | 41.4 | 0 |  | n | 0
2018-02-06 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 986 | 414 | 1400 |  | 0 | 0 | 0 |  | 0 | 295.5 |  | 383.9 | 0 |  | n | 0
2018-02-06 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 735 | 665 | 1400 |  | 0 | 0 | 0 |  | 0 | 36.2 |  | 554.6 | 0 |  | n | 0
2018-02-06 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 605 | 795 | 1400 |  | 0 | 0 | 0 |  | 98.3 | 0 |  | 593.5 | 0 |  | n | 0
2018-02-06 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 437.6 | 0 |  | n | 0
2018-02-06 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 330.8 | 0 |  | n | 0
2018-02-06 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 345 | 0 |  | n | 0
2018-02-06 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 170.6 | 0 |  | n | 0
2018-02-06 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 278.2 | 0 |  | n | 0
2018-02-06 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 917 | 483 | 1400 |  | 0 | 0 | 0 |  | 0 | 223.8 |  | 136.9 | 0 |  | n | 0
2018-02-06 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 45.4 | 0 |  | n | 0
2018-02-06 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 282.6 | 0 |  | n | 0
2018-02-06 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 212 | 1188 | 1400 |  | 0 | 0 | 0 |  | 504.2 | 0 |  | 204 | 0 |  | n | 0
2018-02-06 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 609 | 791 | 1400 |  | 0 | 0 | 0 |  | 94 | 0 |  | 301 | 0 |  | n | 0
2018-02-06 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 380 | 1020 | 1400 |  | 0 | 0 | 0 |  | 330.4 | 0 |  | 0 | 162 |  | n | 0
2018-02-06 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 472 | 928 | 1400 |  | 0 | 0 | 0 |  | 235 | 0 |  | 0 | 70.7 |  | n | 0
2018-02-07 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 157 | 0 |  | n | 0
2018-02-07 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 588 | 812 | 1400 |  | 0 | 0 | 0 |  | 115.7 | 0 |  | 0 | 19 |  | n | 0
2018-02-07 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 570 | 830 | 1400 |  | 0 | 0 | 0 |  | 134.6 | 0 |  | 0 | 0 |  | n | 0
2018-02-07 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 695 | 705 | 1400 |  | 0 | 0 | 0 |  | 5.1 | 0 |  | 0 | 8.2 |  | n | 0
2018-02-07 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 65 | 0 |  | n | 0
2018-02-07 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 110 | 0 |  | n | 0
2018-02-07 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 121 | 1279 | 1400 |  | 0 | 0 | 0 |  | 597.8 | 0 |  | 23.7 | 0 |  | n | 0
2018-02-07 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 2.7 | 0 |  | n | 0
2018-02-07 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 55.1 | 0 |  | n | 0
2018-02-07 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 352 | 1048 | 1400 |  | 0 | 0 | 0 |  | 359.8 | 0 |  | 4.9 | 0 |  | n | 0
2018-02-07 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 32.1 | 0 |  | n | 0
2018-02-07 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 80.6 | 0 |  | n | 0
2018-02-07 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 647 | 753 | 1400 |  | 0 | 0 | 0 |  | 55.2 | 0 |  | 0 | 94.9 |  | n | 0
2018-02-07 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 503 | 897 | 1400 |  | 0 | 0 | 0 |  | 203.2 | 0 |  | 71 | 0 |  | n | 0
2018-02-07 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 406 | 994 | 1400 |  | 0 | 0 | 0 |  | 303.7 | 0 |  | 0 | 33 |  | n | 0
2018-02-07 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 264 | 1136 | 1400 |  | 0 | 0 | 0 |  | 450 | 0 |  | 0 | 30 |  | n | 0
2018-02-07 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 606 | 794 | 1400 |  | 0 | 0 | 0 |  | 97.4 | 0 |  | 11 | 0 |  | n | 0
2018-02-07 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 1 | 0 |  | n | 0
2018-02-07 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 693 | 707 | 1400 |  | 0 | 0 | 0 |  | 7.1 | 0 |  | 0 | 0 |  | n | 0
2018-02-07 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 541 | 859 | 1400 |  | 0 | 0 | 0 |  | 164 | 0 |  | 0 | 0 |  | n | 0
2018-02-07 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 298 | 1102 | 1400 |  | 0 | 0 | 0 |  | 414.8 | 0 |  | 0 | 0 |  | n | 0
2018-02-07 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 35 | 1365 | 1400 |  | 0 | 0 | 0 |  | 687.4 | 0 |  | 35 | 0 |  | n | 0
2018-02-07 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-07 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 99 | 1301 | 1400 |  | 0 | 0 | 0 |  | 621 | 0 |  | 1 | 0 |  | n | 0
2018-02-08 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 2 | 0 |  | 0 | 0 |  | n | 0
2018-02-08 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 401.7 | 0 |  | 0 | 47 |  | n | 0
2018-02-08 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 421.8 | 0 |  | 0 | 83 |  | n | 0
2018-02-08 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 84.5 | 0 |  | 0 | 67 |  | n | 0
2018-02-08 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 94.6 |  | n | 0
2018-02-08 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 126 | 0 |  | 0 | 0 |  | n | 0
2018-02-08 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 397.9 | 0 |  | 0 | 2.2 |  | n | 0
2018-02-08 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 62.9 | 0 |  | 20.3 | 0 |  | n | 0
2018-02-08 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 89 | 0 |  | 35 | 0 |  | n | 0
2018-02-08 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 487.2 | 0 |  | 20 | 0 |  | n | 0
2018-02-08 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 582.8 | 0 |  | 0 | 18 |  | n | 0
2018-02-08 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-08 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-08 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-08 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-08 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-08 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-08 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-08 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-08 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 19 |  | n | 0
2018-02-08 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 21 |  | n | 0
2018-02-08 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 15.8 |  | n | 0
2018-02-08 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 51.1 |  | n | 0
2018-02-08 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 10 |  | n | 0
2018-02-09 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 62 |  | n | 0
2018-02-09 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 62 |  | n | 0
2018-02-09 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 450 | 950 | 1400 |  | 0 | 0 | 0 |  | 258 | 0 |  | 51.9 | 0 |  | n | 0
2018-02-09 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 457 | 943 | 1400 |  | 0 | 0 | 0 |  | 251.5 | 0 |  | 0 | 292.7 |  | n | 0
2018-02-09 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 476 | 924 | 1400 |  | 0 | 0 | 0 |  | 231.8 | 0 |  | 0 | 266.7 |  | n | 0
2018-02-09 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 326 | 1074 | 1400 |  | 0 | 0 | 0 |  | 385.9 | 0 |  | 0 | 274 |  | n | 0
2018-02-09 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 105.8 |  | n | 0
2018-02-09 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 79 |  | n | 0
2018-02-09 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-09 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 10 |  | n | 0
2018-02-10 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 115 |  | n | 0
2018-02-10 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-10 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 496 | 904 | 1400 |  | 0 | 0 | 0 |  | 210.7 | 0 |  | 212 | 0 |  | n | 0
2018-02-10 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 991 | 409 | 1400 |  | 0 | 0 | 0 |  | 0 | 300.8 |  | 273.5 | 0 |  | n | 0
2018-02-11 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 890 | 510 | 1400 |  | 0 | 0 | 0 |  | 0 | 196.6 |  | 0 | 42 |  | n | 0
2018-02-11 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 1032 | 368 | 1400 |  | 0 | 0 | 0 |  | 0 | 343.4 |  | 0 | 55 |  | n | 0
2018-02-11 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 1246 | 154 | 1400 |  | 0 | 0 | 0 |  | 0 | 564.2 |  | 0 | 30 |  | n | 0
2018-02-11 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 1285 | 115 | 1400 |  | 0 | 0 | 0 |  | 0 | 603.9 |  | 0 | 20 |  | n | 0
2018-02-11 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 1234 | 166 | 1400 |  | 0 | 0 | 0 |  | 0 | 551.4 |  | 0 | 20 |  | n | 0
2018-02-11 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-02-11 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 1208 | 192 | 1400 |  | 0 | 0 | 0 |  | 0 | 525 |  | 0 | 0 |  | n | 0
2018-02-11 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-02-11 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 1050 | 350 | 1400 |  | 0 | 0 | 0 |  | 0 | 361.9 |  | 0 | 96.5 |  | n | 0
2018-02-11 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 521 | 879 | 1400 |  | 0 | 0 | 0 |  | 185.1 | 0 |  | 0 | 40.5 |  | n | 0
2018-02-11 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 394 | 1006 | 1400 |  | 0 | 0 | 0 |  | 316.2 | 0 |  | 147.1 | 0 |  | n | 0
2018-02-11 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 246 | 1154 | 1400 |  | 0 | 0 | 0 |  | 469.1 | 0 |  | 198.8 | 0 |  | n | 0
2018-02-11 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 122 | 1278 | 1400 |  | 0 | 0 | 0 |  | 597.4 | 0 |  | 85 | 0 |  | n | 0
2018-02-11 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 317 | 1083 | 1400 |  | 0 | 0 | 0 |  | 395.4 | 0 |  | 68.7 | 0 |  | n | 0
2018-02-11 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 529 | 871 | 1400 |  | 0 | 0 | 0 |  | 176.2 | 0 |  | 124.6 | 0 |  | n | 0
2018-02-11 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 51 | 1349 | 1400 |  | 0 | 0 | 0 |  | 670.8 | 0 |  | 31 | 0 |  | n | 0
2018-02-11 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 17.1 |  | n | 0
2018-02-11 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-11 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-11 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-11 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-11 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-11 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-11 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 37 | 1363 | 1400 |  | 0 | 0 | 0 |  | 684.9 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 9.4 |  | n | 0
2018-02-12 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 30 | 1370 | 1400 |  | 0 | 0 | 0 |  | 692.3 | 0 |  | 30 | 0 |  | n | 0
2018-02-12 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 122 | 1278 | 1400 |  | 0 | 0 | 0 |  | 597.3 | 0 |  | 27.7 | 0 |  | n | 0
2018-02-12 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 1 | 1399 | 1400 |  | 0 | 0 | 0 |  | 722.3 | 0 |  | 1 | 0 |  | n | 0
2018-02-12 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 183 | 1217 | 1400 |  | 0 | 0 | 0 |  | 534 | 0 |  | 183 | 0 |  | n | 0
2018-02-12 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 62 |  | n | 0
2018-02-12 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-12 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 171.3 |  | n | 0
2018-02-13 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-13 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-13 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-13 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-13 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 599 | 0 |  | n | 0
2018-02-13 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 249 | 0 |  | n | 0
2018-02-13 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-13 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 60 | 1340 | 1400 |  | 0 | 0 | 0 |  | 661.6 | 0 |  | 0 | 20 |  | n | 0
2018-02-13 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 625 | 775 | 1400 |  | 0 | 0 | 0 |  | 77.7 | 0 |  | 116.5 | 0 |  | n | 0
2018-02-13 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 572 | 828 | 1400 |  | 0 | 0 | 0 |  | 131.7 | 0 |  | 90.4 | 0 |  | n | 0
2018-02-13 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 616 | 784 | 1400 |  | 0 | 0 | 0 |  | 86.6 | 0 |  | 193.8 | 0 |  | n | 0
2018-02-13 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 667 | 733 | 1400 |  | 0 | 0 | 0 |  | 33.9 | 0 |  | 0 | 133.7 |  | n | 0
2018-02-13 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 139.4 |  | n | 0
2018-02-13 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 557 | 843 | 1400 |  | 0 | 0 | 0 |  | 148.1 | 0 |  | 0 | 119 |  | n | 0
2018-02-13 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 76 |  | n | 0
2018-02-13 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-13 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-13 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 264.8 | 0 |  | n | 0
2018-02-13 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 534 | 866 | 1400 |  | 0 | 0 | 0 |  | 171 | 0 |  | 282 | 0 |  | n | 0
2018-02-13 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-13 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-13 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-13 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-13 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 25 |  | n | 0
2018-02-14 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 614.1 | 0 |  | 104 | 0 |  | n | 0
2018-02-14 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-14 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 680.3 | 0 |  | 0 | 15.7 |  | n | 0
2018-02-15 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 641 | 759 | 1400 |  | 0 | 0 | 0 |  | 61.3 | 0 |  | 0 | 15.7 |  | n | 0
2018-02-15 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 526 | 874 | 1400 |  | 0 | 0 | 0 |  | 179.2 | 0 |  | 45 | 0 |  | n | 0
2018-02-15 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 206 | 1194 | 1400 |  | 0 | 0 | 0 |  | 510.3 | 0 |  | 0 | 58 |  | n | 0
2018-02-15 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 805 | 595 | 1400 |  | 0 | 0 | 0 |  | 0 | 108.7 |  | 0 | 33 |  | n | 0
2018-02-15 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 863 | 537 | 1400 |  | 0 | 0 | 0 |  | 0 | 168.6 |  | 0 | 0 |  | n | 0
2018-02-15 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 592 | 808 | 1400 |  | 0 | 0 | 0 |  | 111.4 | 0 |  | 25.2 | 0 |  | n | 0
2018-02-15 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-15 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 117 |  | n | 0
2018-02-16 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 599 | 0 |  | n | 0
2018-02-16 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 599 | 0 |  | n | 0
2018-02-16 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 65.9 |  | n | 0
2018-02-16 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 208.4 | 0 |  | n | 0
2018-02-16 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 446 |  | n | 0
2018-02-16 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 24 |  | n | 0
2018-02-16 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-16 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 34 | 1366 | 1400 |  | 0 | 0 | 0 |  | 687.5 | 0 |  | 34 | 0 |  | n | 0
2018-02-17 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 634 | 766 | 1400 |  | 0 | 0 | 0 |  | 68.5 | 0 |  | 235 | 0 |  | n | 0
2018-02-17 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 28.9 | 0 |  | n | 0
2018-02-17 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 26.3 | 0 |  | n | 0
2018-02-17 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 257.6 | 0 |  | n | 0
2018-02-17 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 599 | 0 |  | n | 0
2018-02-17 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 700 | 0 |  | n | 0
2018-02-17 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 313 | 1087 | 1400 |  | 0 | 0 | 0 |  | 399.6 | 0 |  | 313 | 0 |  | n | 0
2018-02-17 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 307 | 1093 | 1400 |  | 0 | 0 | 0 |  | 406.2 | 0 |  | 307 | 0 |  | n | 0
2018-02-17 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 362 | 1038 | 1400 |  | 0 | 0 | 0 |  | 348.7 | 0 |  | 267.6 | 0 |  | n | 0
2018-02-17 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-17 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 90 | 1310 | 1400 |  | 0 | 0 | 0 |  | 630.1 | 0 |  | 33.8 | 0 |  | n | 0
2018-02-18 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 233 | 1167 | 1400 |  | 0 | 0 | 0 |  | 482.6 | 0 |  | 233 | 0 |  | n | 0
2018-02-18 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 478.5 | 0 |  | n | 0
2018-02-18 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 22.6 | 0 |  | n | 0
2018-02-18 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 141.8 | 0 |  | n | 0
2018-02-18 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 438.9 | 0 |  | n | 0
2018-02-18 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 354 | 1046 | 1400 |  | 0 | 0 | 0 |  | 357.2 | 0 |  | 332.1 | 0 |  | n | 0
2018-02-18 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-18 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 1 |  | n | 0
2018-02-19 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 255 | 1145 | 1400 |  | 0 | 0 | 0 |  | 459.2 | 0 |  | 0 | 46 |  | n | 0
2018-02-19 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 85 |  | n | 0
2018-02-19 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 118.1 |  | n | 0
2018-02-19 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 75 | 0 |  | n | 0
2018-02-19 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 73 | 1327 | 1400 |  | 0 | 0 | 0 |  | 647.9 | 0 |  | 12.2 | 0 |  | n | 0
2018-02-19 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 162 | 1238 | 1400 |  | 0 | 0 | 0 |  | 556.1 | 0 |  | 93.4 | 0 |  | n | 0
2018-02-19 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-19 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 599 | 0 |  | n | 0
2018-02-20 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 588.1 | 0 |  | n | 0
2018-02-20 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 104 | 1296 | 1400 |  | 0 | 0 | 0 |  | 615.8 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 234 | 1166 | 1400 |  | 0 | 0 | 0 |  | 481 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 267 | 1133 | 1400 |  | 0 | 0 | 0 |  | 447.2 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 261 | 1139 | 1400 |  | 0 | 0 | 0 |  | 453.1 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 25 | 1375 | 1400 |  | 0 | 0 | 0 |  | 697.6 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 190 | 1210 | 1400 |  | 0 | 0 | 0 |  | 527.2 | 0 |  | 190 | 0 |  | n | 0
2018-02-20 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 174 | 1226 | 1400 |  | 0 | 0 | 0 |  | 543.5 | 0 |  | 109 | 0 |  | n | 0
2018-02-20 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 170 | 1230 | 1400 |  | 0 | 0 | 0 |  | 547.2 | 0 |  | 42.1 | 0 |  | n | 0
2018-02-20 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 53 | 1347 | 1400 |  | 0 | 0 | 0 |  | 668.4 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 53 | 1347 | 1400 |  | 0 | 0 | 0 |  | 668.8 | 0 |  | 3 | 0 |  | n | 0
2018-02-20 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-20 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 600 | 800 | 1400 |  | 0 | 0 | 0 |  | 102.9 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 254 | 1146 | 1400 |  | 0 | 0 | 0 |  | 460.8 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 608 | 792 | 1400 |  | 0 | 0 | 0 |  | 94.8 | 0 |  | 52.7 | 0 |  | n | 0
2018-02-21 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 103 | 1297 | 1400 |  | 0 | 0 | 0 |  | 617 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 8 | 1392 | 1400 |  | 0 | 0 | 0 |  | 714.5 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-21 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 124 | 1276 | 1400 |  | 0 | 0 | 0 |  | 594.5 | 0 |  | 0 | 0 |  | n | 0
2018-02-22 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-02-22 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 191 | 1209 | 1400 |  | 0 | 0 | 0 |  | 525.8 | 0 |  | 0 | 99.3 |  | n | 0
2018-02-22 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 364 | 1036 | 1400 |  | 0 | 0 | 0 |  | 347.2 | 0 |  | 0 | 85 |  | n | 0
2018-02-22 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 162 | 1238 | 1400 |  | 0 | 0 | 0 |  | 555.4 | 0 |  | 0 | 45 |  | n | 0
2018-02-22 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 106.6 | 0 |  | n | 0
2018-02-22 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 500 | 900 | 1400 |  | 0 | 0 | 0 |  | 206.2 | 0 |  | 46.6 | 0 |  | n | 0
2018-02-22 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-22 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 84 | 1316 | 1400 |  | 0 | 0 | 0 |  | 635.9 | 0 |  | 0 | 0 |  | n | 0
2018-02-22 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 201 | 1199 | 1400 |  | 0 | 0 | 0 |  | 515.6 | 0 |  | 0 | 10 |  | n | 0
2018-02-22 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 122 | 1278 | 1400 |  | 0 | 0 | 0 |  | 597.1 | 0 |  | 0 | 0 |  | n | 0
2018-02-22 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 91 | 1309 | 1400 |  | 0 | 0 | 0 |  | 629.4 | 0 |  | 0 | 22.5 |  | n | 0
2018-02-22 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 392 | 1008 | 1400 |  | 0 | 0 | 0 |  | 318.6 | 0 |  | 0 | 58.2 |  | n | 0
2018-02-22 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 128 |  | n | 0
2018-02-22 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 59.5 |  | n | 0
2018-02-22 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 557 | 843 | 1400 |  | 0 | 0 | 0 |  | 147.7 | 0 |  | 0 | 80.8 |  | n | 0
2018-02-22 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 40 |  | n | 0
2018-02-22 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 40 |  | n | 0
2018-02-22 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-22 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 37 | 1363 | 1400 |  | 0 | 0 | 0 |  | 685.2 | 0 |  | 0 | 0 |  | n | 0
2018-02-22 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 8.5 |  | n | 0
2018-02-22 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-22 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-22 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 101 | 1299 | 1400 |  | 0 | 0 | 0 |  | 619 | 0 |  | 0 | 35 |  | n | 0
2018-02-22 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 1.5 |  | n | 0
2018-02-23 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 101 | 1299 | 1400 |  | 0 | 0 | 0 |  | 619 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 103 | 1297 | 1400 |  | 0 | 0 | 0 |  | 616.7 | 0 |  | 0.3 | 0 |  | n | 0
2018-02-23 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 41.8 |  | n | 0
2018-02-23 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 70.7 |  | n | 0
2018-02-23 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 64.4 |  | n | 0
2018-02-23 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-23 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 26 |  | n | 0
2018-02-23 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-24 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-24 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-24 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 96.5 |  | n | 0
2018-02-24 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 90 |  | n | 0
2018-02-24 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 267 | 1133 | 1400 |  | 0 | 0 | 0 |  | 447.6 | 0 |  | 0 | 107.9 |  | n | 0
2018-02-24 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 419 | 981 | 1400 |  | 0 | 0 | 0 |  | 290.2 | 0 |  | 0 | 84 |  | n | 0
2018-02-24 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 380 | 1020 | 1400 |  | 0 | 0 | 0 |  | 330.7 | 0 |  | 0 | 88.8 |  | n | 0
2018-02-24 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 232 | 1168 | 1400 |  | 0 | 0 | 0 |  | 483.7 | 0 |  | 0 | 104.5 |  | n | 0
2018-02-24 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 10 |  | n | 0
2018-02-24 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-24 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-24 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 457 | 943 | 1400 |  | 0 | 0 | 0 |  | 251.4 | 0 |  | 0 | 45.1 |  | n | 0
2018-02-24 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 743 | 657 | 1400 |  | 0 | 0 | 0 |  | 0 | 43.9 |  | 0 | 125.1 |  | n | 0
2018-02-24 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 1342 | 58 | 1400 |  | 0 | 0 | 0 |  | 0 | 662.9 |  | 0 | 55.7 |  | n | 0
2018-02-24 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 1013 | 387 | 1400 |  | 0 | 0 | 0 |  | 0 | 323.5 |  | 0 | 15.1 |  | n | 0
2018-02-24 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 18.5 | 0 |  | n | 0
2018-02-24 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 101 | 1299 | 1400 |  | 0 | 0 | 0 |  | 619 | 0 |  | 20 | 0 |  | n | 0
2018-02-24 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-24 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-24 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-24 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-24 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-24 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-24 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 443 | 957 | 1400 |  | 0 | 0 | 0 |  | 265.1 | 0 |  | 108 | 0 |  | n | 0
2018-02-25 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 394 | 1006 | 1400 |  | 0 | 0 | 0 |  | 316.4 | 0 |  | 0 | 206.5 |  | n | 0
2018-02-25 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 993 | 407 | 1400 |  | 0 | 0 | 0 |  | 0 | 302.6 |  | 0 | 208 |  | n | 0
2018-02-25 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 1060 | 340 | 1400 |  | 0 | 0 | 0 |  | 0 | 371.7 |  | 0 | 50 |  | n | 0
2018-02-25 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 901 | 499 | 1400 |  | 0 | 0 | 0 |  | 0 | 208.1 |  | 0 | 32.7 |  | n | 0
2018-02-25 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 290 | 1110 | 1400 |  | 0 | 0 | 0 |  | 423.3 | 0 |  | 177 | 0 |  | n | 0
2018-02-25 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 96 | 1304 | 1400 |  | 0 | 0 | 0 |  | 623.9 | 0 |  | 1.5 | 0 |  | n | 0
2018-02-25 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 695 | 705 | 1400 |  | 0 | 0 | 0 |  | 4.9 | 0 |  | 0.5 | 0 |  | n | 0
2018-02-25 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 1295 | 105 | 1400 |  | 0 | 0 | 0 |  | 0 | 614.1 |  | 91 | 0 |  | n | 0
2018-02-25 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 1070 | 330 | 1400 |  | 0 | 0 | 0 |  | 0 | 382.6 |  | 191.3 | 0 |  | n | 0
2018-02-25 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 421 | 0 |  | n | 0
2018-02-25 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 101 | 1299 | 1400 |  | 0 | 0 | 0 |  | 619 | 0 |  | 101 | 0 |  | n | 0
2018-02-25 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-25 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 373 | 1027 | 1400 |  | 0 | 0 | 0 |  | 337.3 | 0 |  | 373 | 0 |  | n | 0
2018-02-26 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 168.8 |  | n | 0
2018-02-26 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 167.3 |  | n | 0
2018-02-26 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-26 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 25 |  | n | 0
2018-02-27 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-27 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 20 |  | n | 0
2018-02-28 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 109 |  | n | 0
2018-02-28 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 252.8 |  | n | 0
2018-02-28 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 258.2 |  | n | 0
2018-02-28 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 236.5 |  | n | 0
2018-02-28 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 59.2 |  | n | 0
2018-02-28 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 245.3 |  | n | 0
2018-02-28 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 247 | 1153 | 1400 |  | 0 | 0 | 0 |  | 467.8 | 0 |  | 25.1 | 0 |  | n | 0
2018-02-28 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 3.7 | 0 |  | n | 0
2018-02-28 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 172.3 | 0 |  | n | 0
2018-02-28 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 400 | 0 |  | n | 0
2018-02-28 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-02-28 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 68 | 1332 | 1400 |  | 0 | 0 | 0 |  | 652.8 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 338 | 1062 | 1400 |  | 0 | 0 | 0 |  | 373.9 | 0 |  | 239.7 | 0 |  | n | 0
2018-03-01 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 937 | 463 | 1400 |  | 0 | 0 | 0 |  | 0 | 245.1 |  | 603.8 | 0 |  | n | 0
2018-03-01 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 1397 | 3 | 1400 |  | 0 | 0 | 0 |  | 0 | 720 |  | 809.4 | 0 |  | n | 0
2018-03-01 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 799 | 601 | 1400 |  | 0 | 0 | 0 |  | 0 | 102.7 |  | 134.7 | 0 |  | n | 0
2018-03-01 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 317 | 1083 | 1400 |  | 0 | 0 | 0 |  | 395.2 | 0 |  | 6.5 | 0 |  | n | 0
2018-03-01 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 186 | 1214 | 1400 |  | 0 | 0 | 0 |  | 530.8 | 0 |  | 2 | 0 |  | n | 0
2018-03-01 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-01 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 364.7 |  | n | 0
2018-03-02 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 363.1 |  | n | 0
2018-03-02 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 374 | 1026 | 1400 |  | 0 | 0 | 0 |  | 336.7 | 0 |  | 0 | 135 |  | n | 0
2018-03-02 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 474 | 926 | 1400 |  | 0 | 0 | 0 |  | 233.1 | 0 |  | 0 | 26.3 |  | n | 0
2018-03-02 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 516 | 884 | 1400 |  | 0 | 0 | 0 |  | 190.5 | 0 |  | 0 | 106.3 |  | n | 0
2018-03-02 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 568 | 832 | 1400 |  | 0 | 0 | 0 |  | 136.6 | 0 |  | 79.6 | 0 |  | n | 0
2018-03-02 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-02 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 124 | 1276 | 1400 |  | 0 | 0 | 0 |  | 594.7 | 0 |  | 124 | 0 |  | n | 0
2018-03-03 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 54 | 1346 | 1400 |  | 0 | 0 | 0 |  | 667.5 | 0 |  | 54 | 0 |  | n | 0
2018-03-03 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 201 | 1199 | 1400 |  | 0 | 0 | 0 |  | 515.9 | 0 |  | 201 | 0 |  | n | 0
2018-03-03 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 225 | 1175 | 1400 |  | 0 | 0 | 0 |  | 491.1 | 0 |  | 225 | 0 |  | n | 0
2018-03-03 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-03 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-03-04 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 29 | 671 | 700 |  | 700 | 0 | 0 |  | 692.9 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 197 | 503 | 700 |  | 700 | 0 | 0 |  | 519.7 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 574 | 126 | 700 |  | 700 | 0 | 0 |  | 129.9 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 563 | 137 | 700 |  | 700 | 0 | 0 |  | 141.9 | 0 |  | 3.7 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 349 | 351 | 700 |  | 700 | 0 | 0 |  | 362.8 | 0 |  | 348.5 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 244 | 456 | 700 |  | 700 | 0 | 0 |  | 470.6 | 0 |  | 244 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-04 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 452 | 248 | 700 |  | 700 | 0 | 0 |  | 256.3 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 567 | 133 | 700 |  | 700 | 0 | 0 |  | 137.6 | 0 |  | 0 | 10 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 685 | 15 | 700 |  | 700 | 0 | 0 |  | 15.8 | 0 |  | 0 | 10 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 599 | 101 | 700 |  | 700 | 0 | 0 |  | 104 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 103 | 597 | 700 |  | 700 | 0 | 0 |  | 616.7 | 0 |  | 103 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 700 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 700 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 650.5 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 484.3 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 599 | 101 | 700 |  | 700 | 0 | 0 |  | 104 | 0 |  | 599 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-05 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 560 | 140 | 700 |  | 700 | 0 | 0 |  | 144.9 | 0 |  | 451.4 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 270.7 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 11 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 1.8 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 20 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 62.5 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 180 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 158 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 170 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 162.3 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 130 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 180 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 188 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 599 | 401 | 1000 |  | 700 | 0 | 0 |  | 104 | 0 |  | 281 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 1000 | 1000 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 1000 | 1000 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 1000 | 1000 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 1000 | 1000 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-06 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 1000 | 1000 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 599 | 101 | 700 |  | 700 | 0 | 0 |  | 104 | 0 |  | 150 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 405 | 295 | 700 |  | 700 | 0 | 0 |  | 305.2 | 0 |  | 186.6 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 412.7 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 78 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 100 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 111 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 199 | 801 | 1000 |  | 700 | 0 | 0 |  | 517.7 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 88 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 65 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 391 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 689 | 311 | 1000 |  | 700 | 0 | 0 |  | 11.1 | 0 |  | 689 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 155.1 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 684 | 316 | 1000 |  | 700 | 0 | 0 |  | 16.3 | 0 |  | 684 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 638.4 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 528.3 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 422.6 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 300 | 1000 |  | 700 | 0 | 0 |  | 0 | 0 |  | 417.5 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 664 | 336 | 1000 |  | 700 | 0 | 0 |  | 37.1 | 0 |  | 78.4 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 599 | 401 | 1000 |  | 700 | 0 | 0 |  | 104 | 0 |  | 102.2 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 1000 | 1000 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 116.9 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 1000 | 1000 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 174.6 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 523 | 477 | 1000 |  | 700 | 0 | 0 |  | 182.5 | 0 |  | 120 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 1000 | 1000 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-07 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 599 | 101 | 700 |  | 700 | 0 | 0 |  | 104 | 0 |  | 151.6 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 618 | 82 | 700 |  | 700 | 0 | 0 |  | 84.9 | 0 |  | 46.6 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 69 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 573 | 127 | 700 |  | 700 | 0 | 0 |  | 131.1 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 479 | 221 | 700 |  | 700 | 0 | 0 |  | 228.3 | 0 |  | 35 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 383 | 317 | 700 |  | 700 | 0 | 0 |  | 327.8 | 0 |  | 264.2 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 285 | 415 | 700 |  | 700 | 0 | 0 |  | 429 | 0 |  | 240.5 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 55 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 165 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 505 | 195 | 700 |  | 700 | 0 | 0 |  | 200.9 | 0 |  | 0 | 0.1 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 601 | 99 | 700 |  | 700 | 0 | 0 |  | 102.1 | 0 |  | 0 | 94.3 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 429 | 271 | 700 |  | 700 | 0 | 0 |  | 279.8 | 0 |  | 0 | 66.7 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 38 | 662 | 700 |  | 700 | 0 | 0 |  | 683.4 | 0 |  | 0 | 264.8 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 101 | 599 | 700 |  | 700 | 0 | 0 |  | 619 | 0 |  | 0 | 168.6 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 50 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 568 | 132 | 700 |  | 700 | 0 | 0 |  | 136.7 | 0 |  | 0 | 132 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-08 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 340 | 360 | 700 |  | 700 | 0 | 0 |  | 372 | 0 |  | 0 | 332.6 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 101 | 599 | 700 |  | 700 | 0 | 0 |  | 619 | 0 |  | 1.5 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 94 | 606 | 700 |  | 700 | 0 | 0 |  | 626.4 | 0 |  | 94 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 239 | 461 | 700 |  | 700 | 0 | 0 |  | 476.5 | 0 |  | 238 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 291 | 409 | 700 |  | 700 | 0 | 0 |  | 422.4 | 0 |  | 291 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 76 | 624 | 700 |  | 700 | 0 | 0 |  | 645.1 | 0 |  | 0 | 30 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 128 | 572 | 700 |  | 700 | 0 | 0 |  | 590.7 | 0 |  | 10 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 140 | 560 | 700 |  | 700 | 0 | 0 |  | 578.5 | 0 |  | 140 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-09 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 230 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 527 | 173 | 700 |  | 700 | 0 | 0 |  | 179.2 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 122 | 578 | 700 |  | 700 | 0 | 0 |  | 597.3 | 0 |  | 20 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 586 | 114 | 700 |  | 700 | 0 | 0 |  | 117.2 | 0 |  | 0 | 30.4 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 605 | 95 | 700 |  | 700 | 0 | 0 |  | 98.3 | 0 |  | 0 | 8 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 599 | 101 | 700 |  | 700 | 0 | 0 |  | 104 | 0 |  | 0 | 1.5 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 420 | 280 | 700 |  | 700 | 0 | 0 |  | 289.7 | 0 |  | 420 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 325 | 375 | 700 |  | 700 | 0 | 0 |  | 387.1 | 0 |  | 0 | 74.6 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 60 | 640 | 700 |  | 700 | 0 | 0 |  | 661.6 | 0 |  | 0 | 95.6 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-10 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 389 | 311 | 700 |  | 700 | 0 | 0 |  | 321.1 | 0 |  | 0 | 113.3 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 30 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 132.5 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 599 | 101 | 700 |  | 700 | 0 | 0 |  | 104 | 0 |  | 169.7 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 169 | 531 | 700 |  | 700 | 0 | 0 |  | 548.3 | 0 |  | 169 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 125.5 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-11 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/3 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 0 | 0 |  | 0 | 0 |  | 67.1 | 0 |  | n | 0 | 300kV line Bamble-Porsgrunn is disconnected in the period.
2018-03-12 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 723 | 0 | 723 | 700 | 0 | 700 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | j | 700 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 723 | 0 | 723 | 642 | 58 | 700 |  | 700 | 700 | 700 |  | 59.6 | 0 |  | 0 | 58 |  | j | 700 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 723 | 0 | 723 | 43 | 657 | 700 |  | 700 | 700 | 700 |  | 678.6 | 0 |  | 0 | 226.8 |  | j | 700 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 700 | 700 |  | 723 | 0 |  | 0 | 320 |  | j | 700 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 723 | 0 | 723 | 167 | 533 | 700 |  | 700 | 700 | 700 |  | 550.2 | 0 |  | 0 | 393.3 |  | j | 700 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 723 | 0 | 723 | 599 | 101 | 700 |  | 700 | 700 | 700 |  | 104 | 0 |  | 0 | 1.5 |  | j | 700 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 723 | 0 | 723 | 0 | 700 | 700 |  | 700 | 700 | 700 |  | 723 | 0 |  | 0 | 0 |  | j | 700 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 100 | 100 | 200 |  | 700 | 700 | 700 |  | 103.4 | 0 |  | 0 | 8.5 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 0 | 199 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 0 | 199 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 200 | 0 | 200 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 200 | 0 | 200 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 0 | 104 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 200 | 0 | 200 |  | 700 | 700 | 700 |  | 0 | 0 |  | 72.2 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 0 | 13.7 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-12 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 187 | 13 | 200 |  | 700 | 700 | 700 |  | 13 | 0 |  | 62 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 200 | 0 | 200 |  | 700 | 700 | 700 |  | 0 | 0 |  | 200 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 200 | 0 | 200 |  | 700 | 700 | 700 |  | 0 | 0 |  | 60 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 200 | 0 | 200 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 200 | 0 | 200 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 200 | 0 | 200 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 43 | 157 | 200 |  | 700 | 700 | 700 |  | 162.6 | 0 |  | 43 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-13 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 0 | 206 | 1 | 199 | 200 |  | 700 | 700 | 700 |  | 206 | 0 |  | 1 | 0 |  | j | 200 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1 Manual adjustment due to the fact that a part of the non availability is due to Norwegian grid restrictions.
2018-03-14 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 200 | 200 | 400 |  | 501 | 501 | 501 |  | 0 | 0 |  | 30.2 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 278 | 122 | 400 |  | 501 | 501 | 501 |  | 0 | 80.7 |  | 0 | 19.4 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 10 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 19 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 200 | 200 | 400 |  | 501 | 501 | 501 |  | 0 | 0 |  | 0 | 100.9 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 183 | 217 | 400 |  | 501 | 501 | 501 |  | 17.3 | 0 |  | 0 | 15 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 200 | 200 | 400 |  | 501 | 501 | 501 |  | 0 | 0 |  | 0 | 7.1 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 162 | 238 | 400 |  | 501 | 501 | 501 |  | 39 | 0 |  | 20 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 71.6 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 66 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 72 | 328 | 400 |  | 501 | 501 | 501 |  | 132.3 | 0 |  | 47 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 77 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 33.5 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-14 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 399 | 1 | 400 |  | 501 | 501 | 501 |  | 0 | 206 |  | 0 | 1 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 399 | 1 | 400 |  | 501 | 501 | 501 |  | 0 | 206 |  | 0 | 1 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 399 | 1 | 400 |  | 501 | 501 | 501 |  | 0 | 206 |  | 0 | 1 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 399 | 1 | 400 |  | 501 | 501 | 501 |  | 0 | 206 |  | 0 | 1 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 399 | 1 | 400 |  | 501 | 501 | 501 |  | 0 | 206 |  | 0 | 1 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 399 | 1 | 400 |  | 501 | 501 | 501 |  | 0 | 206 |  | 0 | 1 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 399 | 1 | 400 |  | 501 | 501 | 501 |  | 0 | 206 |  | 0 | 1 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 140 | 260 | 400 |  | 501 | 501 | 501 |  | 62.4 | 0 |  | 0 | 10 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 399 | 400 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 99 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-15 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 127.9 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 206 | 412 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 1.6 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-16 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 60 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 307 | 593 | 900 |  | 501 | 501 | 501 |  | 0 | 110.6 |  | 0 | 265.4 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 759 | 141 | 900 |  | 501 | 501 | 501 |  | 0 | 577.8 |  | 0 | 89.1 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 0 | 345.4 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 136.9 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-17 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 117 | 783 | 900 |  | 501 | 501 | 501 |  | 86.2 | 0 |  | 93.3 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 200 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 182 | 718 | 900 |  | 501 | 501 | 501 |  | 19 | 0 |  | 179.7 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 47 | 853 | 900 |  | 501 | 501 | 501 |  | 158.4 | 0 |  | 47 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 340 | 560 | 900 |  | 501 | 501 | 501 |  | 0 | 144.3 |  | 340 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 440 | 460 | 900 |  | 501 | 501 | 501 |  | 0 | 248.2 |  | 88.5 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 277 | 623 | 900 |  | 501 | 501 | 501 |  | 0 | 79.9 |  | 13.6 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 220 | 680 | 900 |  | 501 | 501 | 501 |  | 0 | 20.6 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 108 | 792 | 900 |  | 501 | 501 | 501 |  | 94.9 | 0 |  | 108 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 658 | 242 | 900 |  | 501 | 501 | 501 |  | 0 | 472.9 |  | 398.6 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 900 | 0 | 900 |  | 501 | 501 | 501 |  | 0 | 723 |  | 900 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 900 | 0 | 900 |  | 501 | 501 | 501 |  | 0 | 723 |  | 676.7 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 900 | 0 | 900 |  | 501 | 501 | 501 |  | 0 | 723 |  | 548.5 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 900 | 0 | 900 |  | 501 | 501 | 501 |  | 0 | 723 |  | 678.7 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 900 | 0 | 900 |  | 501 | 501 | 501 |  | 0 | 723 |  | 664.2 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 604 | 296 | 900 |  | 501 | 501 | 501 |  | 0 | 417.5 |  | 416 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 84 | 816 | 900 |  | 501 | 501 | 501 |  | 119.5 | 0 |  | 84 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 200 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-18 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 148 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 136 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 200 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-19 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 200 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 200 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 172.6 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 108.3 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 1 | 899 | 900 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 97 | 803 | 900 |  | 501 | 501 | 501 |  | 106.7 | 0 |  | 97 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 42 | 858 | 900 |  | 501 | 501 | 501 |  | 163.2 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 22.1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 200 | 700 | 900 |  | 501 | 501 | 501 |  | 0 | 0 |  | 0 | 105 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 7 | 7 |  | 501 | 501 | 501 |  | 7.6 | 0 |  | 0 | 18.1 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 0 | 0 |  | 501 | 501 | 501 |  | 0 | 0 |  | 200 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 0 | 0 |  | 501 | 501 | 501 |  | 0 | 0 |  | 200 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 0 | 0 |  | 501 | 501 | 501 |  | 0 | 0 |  | 200 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 0 | 0 |  | 501 | 501 | 501 |  | 0 | 0 |  | 200 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 1 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-20 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 192 | 192 |  | 501 | 501 | 501 |  | 197.8 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 0 | 0 |  | 501 | 501 | 501 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 0 | 0 |  | 501 | 501 | 501 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 0 | 0 |  | 501 | 501 | 501 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 0 | 0 |  | 501 | 501 | 501 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-21 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/fd6828c6-7138-4d70-88d2-8270bf6f7312/2 | 206 | 723 | 929 | 0 | 199 | 199 |  | 501 | 501 | 501 |  | 206 | 0 |  | 0 | 0 |  | n | 0 | The capacity NO2-NL is reduced because of maintenance work in the Dutch grid, the 380 kV line Zwolle-Meeden is disconnected. Statnett also has work that affects the transmission capacity NO2-NL during the same period, (maintenance work on the 300 kV line Bamble-Porsgrunn and test of the new Scada-system). See the UMM: https://umm.nordpoolgroup.com/#/messages/515244f5-a787-4582-bbdf-4746db9fd943/1 and https://umm.nordpoolgroup.com/#/messages/564c7a82-9301-4e44-aab5-75090a49e17e/1
2018-03-22 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-22 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-23 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-24 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 02 - 03 | n | n | [18 empty] | n | 0 | Change from winter time to summer time.
2018-03-25 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-25 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-26 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-27 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-28 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-29 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-30 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-03-31 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-01 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-02 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-03 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-04 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-05 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-06 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-07 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-08 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-09 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-10 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-11 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-12 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-13 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-14 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-15 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-16 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-17 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-18 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-19 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-20 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-21 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-22 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-23 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-24 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-25 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/388bf537-ff1c-4f10-8f7f-eeba62cb7047/6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Failure on the NorNed cable on the Dutch side.
2018-04-26 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1091 | 109 | 1200 |  | 200 | 0 | 0 |  | 0 | 610.9 |  | 0 | 9.5 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-26 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-26 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-26 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-26 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-26 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-26 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 114 | 1086 | 1200 |  | 200 | 0 | 0 |  | 398.6 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 410 | 790 | 1200 |  | 200 | 0 | 0 |  | 92.7 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 447 | 753 | 1200 |  | 200 | 0 | 0 |  | 54.3 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 754 | 446 | 1200 |  | 200 | 0 | 0 |  | 0 | 262.5 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1033 | 167 | 1200 |  | 200 | 0 | 0 |  | 0 | 550.4 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 36 | 1164 | 1200 |  | 200 | 0 | 0 |  | 479.3 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 729 | 471 | 1200 |  | 200 | 0 | 0 |  | 0 | 236.2 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 824 | 376 | 1200 |  | 200 | 0 | 0 |  | 0 | 334.4 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-27 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 302 | 898 | 1200 |  | 200 | 0 | 0 |  | 204.2 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 154 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 976 | 224 | 1200 |  | 200 | 0 | 0 |  | 0 | 491.9 |  | 0 | 163 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 898 | 302 | 1200 |  | 200 | 0 | 0 |  | 0 | 411.4 |  | 0 | 249.7 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 799 | 401 | 1200 |  | 200 | 0 | 0 |  | 0 | 309 |  | 0 | 221.8 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1033 | 167 | 1200 |  | 200 | 0 | 0 |  | 0 | 550.2 |  | 0 | 167 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1200 | 0 | 1200 |  | 200 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 951 | 249 | 1200 |  | 200 | 0 | 0 |  | 0 | 466 |  | 0 | 133.8 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 129.4 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 119.7 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 634 | 566 | 1200 |  | 200 | 0 | 0 |  | 0 | 138.4 |  | 0 | 71 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 966 | 234 | 1200 |  | 200 | 0 | 0 |  | 0 | 481 |  | 0 | 117.8 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 938 | 262 | 1200 |  | 200 | 0 | 0 |  | 0 | 452.8 |  | 0 | 176 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1158 | 42 | 1200 |  | 200 | 0 | 0 |  | 0 | 679.9 |  | 0 | 42 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1200 | 0 | 1200 |  | 200 | 0 | 0 |  | 0 | 723 |  | 40 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1200 | 0 | 1200 |  | 200 | 0 | 0 |  | 0 | 723 |  | 16.3 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1200 | 0 | 1200 |  | 200 | 0 | 0 |  | 0 | 723 |  | 80 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 884 | 316 | 1200 |  | 200 | 0 | 0 |  | 0 | 396.5 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 285 | 915 | 1200 |  | 200 | 0 | 0 |  | 222.5 | 0 |  | 1.5 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-28 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 500 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 20.1 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 409 | 791 | 1200 |  | 200 | 0 | 0 |  | 94 | 0 |  | 0 | 190.2 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 82.9 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 37.5 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 75.3 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 196 | 1004 | 1200 |  | 200 | 0 | 0 |  | 314.2 | 0 |  | 0 | 122.1 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 213 | 987 | 1200 |  | 200 | 0 | 0 |  | 296.9 | 0 |  | 0 | 121 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 37 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 242 | 958 | 1200 |  | 200 | 0 | 0 |  | 266.8 | 0 |  | 15.4 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 40 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 667 | 533 | 1200 |  | 200 | 0 | 0 |  | 0 | 172.2 |  | 170 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 40 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 120 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 718 | 482 | 1200 |  | 200 | 0 | 0 |  | 0 | 224.8 |  | 250 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 893 | 307 | 1200 |  | 200 | 0 | 0 |  | 0 | 406.1 |  | 251.3 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1133 | 67 | 1200 |  | 200 | 0 | 0 |  | 0 | 653.5 |  | 195 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1200 | 0 | 1200 |  | 200 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 952 | 248 | 1200 |  | 200 | 0 | 0 |  | 0 | 467.3 |  | 253 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 928 | 272 | 1200 |  | 200 | 0 | 0 |  | 0 | 442.2 |  | 0 | 11.2 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1200 | 0 | 1200 |  | 200 | 0 | 0 |  | 0 | 723 |  | 5.4 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1200 | 0 | 1200 |  | 200 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 614 | 586 | 1200 |  | 200 | 0 | 0 |  | 0 | 117.8 |  | 14.5 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 475 | 725 | 1200 |  | 200 | 0 | 0 |  | 25.4 | 0 |  | 138 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-29 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 345 | 855 | 1200 |  | 200 | 0 | 0 |  | 160.5 | 0 |  | 39 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 714 | 486 | 1200 |  | 200 | 0 | 0 |  | 0 | 221.5 |  | 0 | 192.5 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 693 | 507 | 1200 |  | 200 | 0 | 0 |  | 0 | 198.9 |  | 0 | 507 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1082 | 118 | 1200 |  | 200 | 0 | 0 |  | 0 | 601.2 |  | 0 | 118 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1200 | 0 | 1200 |  | 200 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 917 | 283 | 1200 |  | 200 | 0 | 0 |  | 0 | 430.6 |  | 0 | 283 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 471 | 729 | 1200 |  | 200 | 0 | 0 |  | 29.6 | 0 |  | 0 | 228.3 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 98.8 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 227 | 973 | 1200 |  | 200 | 0 | 0 |  | 282.1 | 0 |  | 227 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 124 | 1076 | 1200 |  | 200 | 0 | 0 |  | 388 | 0 |  | 124 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 456 | 744 | 1200 |  | 200 | 0 | 0 |  | 45.8 | 0 |  | 360 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 698 | 502 | 1200 |  | 200 | 0 | 0 |  | 0 | 204.8 |  | 471.5 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 480 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 461 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 255 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-04-30 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 518 | 682 | 1200 |  | 200 | 0 | 0 |  | 0 | 18.4 |  | 0 | 15 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 646 | 554 | 1200 |  | 200 | 0 | 0 |  | 0 | 151.2 |  | 0 | 21.4 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 522 | 678 | 1200 |  | 200 | 0 | 0 |  | 0 | 22.6 |  | 0 | 97.5 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 523 | 677 | 1200 |  | 200 | 0 | 0 |  | 0 | 23.7 |  | 18 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 45.4 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 115.7 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 147 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 202 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 115 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-01 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 50 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 550 | 650 | 1200 |  | 200 | 0 | 0 |  | 0 | 51.5 |  | 0 | 48.5 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1149 | 51 | 1200 |  | 200 | 0 | 0 |  | 0 | 670.5 |  | 33 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1200 | 0 | 1200 |  | 200 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 1187 | 13 | 1200 |  | 200 | 0 | 0 |  | 0 | 709.7 |  | 53.6 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 683 | 517 | 1200 |  | 200 | 0 | 0 |  | 0 | 189.1 |  | 0 | 1.5 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 84 | 1116 | 1200 |  | 200 | 0 | 0 |  | 429.9 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 248.5 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 29.7 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 346.2 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 127 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 372 | 828 | 1200 |  | 200 | 0 | 0 |  | 132.6 | 0 |  | 62.4 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-02 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 263 | 937 | 1200 |  | 200 | 0 | 0 |  | 244.7 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 57 | 1143 | 1200 |  | 200 | 0 | 0 |  | 457.3 | 0 |  | 40.5 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 50 | 1017 | 1067 |  | 200 | 0 | 0 |  | 327.8 | 0 |  | 50 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 30 | 913 | 943 |  | 200 | 0 | 0 |  | 219.6 | 0 |  | 30 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 754 | 754 |  | 200 | 0 | 0 |  | 55.2 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 700 | 700 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-03 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 309.2 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 69.5 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 43.2 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 804 | 396 | 1200 |  | 200 | 0 | 0 |  | 0 | 314.4 |  | 86.1 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 205 | 995 | 1200 |  | 200 | 0 | 0 |  | 304.6 | 0 |  | 34 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-04 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 10 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 21 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 107.3 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 57 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 1.6 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 45 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 65 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 35 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 76 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 741 | 459 | 1200 |  | 200 | 0 | 0 |  | 0 | 249.2 |  | 0 | 35.4 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 837 | 363 | 1200 |  | 200 | 0 | 0 |  | 0 | 348.1 |  | 116.8 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 855 | 345 | 1200 |  | 200 | 0 | 0 |  | 0 | 367.1 |  | 0 | 99.2 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 864 | 336 | 1200 |  | 200 | 0 | 0 |  | 0 | 375.6 |  | 0 | 336 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 785 | 415 | 1200 |  | 200 | 0 | 0 |  | 0 | 294.7 |  | 0 | 415 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 443 | 757 | 1200 |  | 200 | 0 | 0 |  | 59 | 0 |  | 0 | 444 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 100.5 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 8.8 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 41 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 45 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-05 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 328 | 872 | 1200 |  | 200 | 0 | 0 |  | 177.6 | 0 |  | 0 | 150 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 48 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 73.9 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 472 | 728 | 1200 |  | 200 | 0 | 0 |  | 29.2 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 305 | 895 | 1200 |  | 200 | 0 | 0 |  | 201.1 | 0 |  | 0 | 20 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 474 | 726 | 1200 |  | 200 | 0 | 0 |  | 27.2 | 0 |  | 80 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 11 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 118 | 1082 | 1200 |  | 200 | 0 | 0 |  | 394.1 | 0 |  | 0 | 304.3 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 232 | 968 | 1200 |  | 200 | 0 | 0 |  | 276.8 | 0 |  | 0 | 379.9 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 287 | 913 | 1200 |  | 200 | 0 | 0 |  | 219.9 | 0 |  | 0 | 59 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 110.4 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 214 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 219.5 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 276 | 924 | 1200 |  | 200 | 0 | 0 |  | 231.7 | 0 |  | 0 | 34.9 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 34 | 1166 | 1200 |  | 200 | 0 | 0 |  | 481.6 | 0 |  | 0 | 589.4 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 160 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 33.2 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-06 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 76 | 1124 | 1200 |  | 200 | 0 | 0 |  | 437.6 | 0 |  | 75.3 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 20 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-07 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 10 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-08 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-09 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-10 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-11 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 20 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 21 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 26.1 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 16 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 190 | 1010 | 1200 |  | 200 | 0 | 0 |  | 320.6 | 0 |  | 60 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 20.8 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-12 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 477 | 723 | 1200 |  | 200 | 0 | 0 |  | 24.1 | 0 |  | 319.5 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 150.8 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 95.6 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-13 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 92 | 1108 | 1200 |  | 200 | 0 | 0 |  | 421.2 | 0 |  | 70 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 320 | 880 | 1200 |  | 200 | 0 | 0 |  | 185.6 | 0 |  | 320 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 273 | 927 | 1200 |  | 200 | 0 | 0 |  | 234.2 | 0 |  | 217.5 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 60 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 23.8 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-14 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 97 | 1103 | 1200 |  | 200 | 0 | 0 |  | 416.8 | 0 |  | 97 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 36 | 1164 | 1200 |  | 200 | 0 | 0 |  | 479.2 | 0 |  | 36 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 28 | 1172 | 1200 |  | 200 | 0 | 0 |  | 488 | 0 |  | 0 | 74 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 0 | 190 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 99 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 500 | 700 | 1200 |  | 200 | 0 | 0 |  | 0 | 0 |  | 220 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-15 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 67 | 1133 | 1200 |  | 200 | 0 | 0 |  | 447 | 0 |  | 67 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 0 | 1200 | 1200 |  | 200 | 0 | 0 |  | 516 | 0 |  | 0 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 54 | 1146 | 1200 |  | 200 | 0 | 0 |  | 460.4 | 0 |  | 42 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/2214a2ed-760f-4944-98d0-ca9b51c08b59/6 | 516 | 723 | 1239 | 186 | 1014 | 1200 |  | 200 | 0 | 0 |  | 324.7 | 0 |  | 186 | 0 |  | n | 0 | Due to work with the new overheadline 420 kV Lyse-Ertsmyra the 300 kV Lyse-Tonstad needs to be taken out of operation due to short distans between the to lines. Tonstad-T_Tjørhom-Tjørhom is only going to be disconected during the looping to make it possible for Tjørhom power station to produce to Tonstad (23/4 at 15:00-18/5 at 08:00 CEST). Reduction on SK is due to high load on Lyse-Duge due to this and other outage in the grid (300 kV Stokkeland-Tonstad and 420 kV Kvilldal-Holen).
2018-05-16 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 596 | 804 | 1400 |  | 0 | 0 | 0 |  | 107.1 | 0 |  | 396 | 0 |  | n | 0
2018-05-16 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-16 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-16 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-16 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-16 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-16 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 81 | 1319 | 1400 |  | 0 | 0 | 0 |  | 639.5 | 0 |  | 81 | 0 |  | n | 0
2018-05-17 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 96.6 |  | n | 0
2018-05-17 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-17 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 60 |  | n | 0
2018-05-18 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 4.5 |  | n | 0
2018-05-18 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-18 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 539.1 |  | n | 0
2018-05-19 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 124.2 |  | n | 0
2018-05-19 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 169.7 |  | n | 0
2018-05-19 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 303.4 |  | n | 0
2018-05-19 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 294.2 |  | n | 0
2018-05-19 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 235.5 |  | n | 0
2018-05-19 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 276.2 |  | n | 0
2018-05-19 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 227.4 |  | n | 0
2018-05-19 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 80.3 |  | n | 0
2018-05-19 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-19 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-20 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 18 |  | n | 0
2018-05-20 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-20 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-20 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 37 |  | n | 0
2018-05-20 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-20 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-20 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 44 |  | n | 0
2018-05-20 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 37.8 |  | n | 0
2018-05-20 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 36 |  | n | 0
2018-05-20 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 16 |  | n | 0
2018-05-20 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 137 | 1263 | 1400 |  | 0 | 0 | 0 |  | 581.1 | 0 |  | 0 | 5 |  | n | 0
2018-05-20 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 63 | 1337 | 1400 |  | 0 | 0 | 0 |  | 657.9 | 0 |  | 0 | 261.9 |  | n | 0
2018-05-20 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 44 | 1356 | 1400 |  | 0 | 0 | 0 |  | 677.5 | 0 |  | 0 | 350.4 |  | n | 0
2018-05-20 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 131 | 1269 | 1400 |  | 0 | 0 | 0 |  | 587.5 | 0 |  | 0 | 367.7 |  | n | 0
2018-05-20 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 169 | 1231 | 1400 |  | 0 | 0 | 0 |  | 548.3 | 0 |  | 0 | 207.1 |  | n | 0
2018-05-20 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 112 | 1288 | 1400 |  | 0 | 0 | 0 |  | 607.8 | 0 |  | 0 | 419.6 |  | n | 0
2018-05-20 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 641.7 |  | n | 0
2018-05-20 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 185.9 |  | n | 0
2018-05-20 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 235.2 |  | n | 0
2018-05-20 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-20 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-20 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-20 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-20 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 143 | 1257 | 1400 |  | 0 | 0 | 0 |  | 575.3 | 0 |  | 0 | 174.4 |  | n | 0
2018-05-21 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 94 | 1306 | 1400 |  | 0 | 0 | 0 |  | 626.4 | 0 |  | 0 | 201.5 |  | n | 0
2018-05-21 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 693 | 707 | 1400 |  | 0 | 0 | 0 |  | 7.4 | 0 |  | 165.5 | 0 |  | n | 0
2018-05-21 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 1169 | 231 | 1400 |  | 0 | 0 | 0 |  | 0 | 484 |  | 188.5 | 0 |  | n | 0
2018-05-21 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 983 | 417 | 1400 |  | 0 | 0 | 0 |  | 0 | 292.6 |  | 225.5 | 0 |  | n | 0
2018-05-21 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 452 | 948 | 1400 |  | 0 | 0 | 0 |  | 255.7 | 0 |  | 188.8 | 0 |  | n | 0
2018-05-21 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 70 | 1330 | 1400 |  | 0 | 0 | 0 |  | 651.3 | 0 |  | 70 | 0 |  | n | 0
2018-05-21 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 482 | 918 | 1400 |  | 0 | 0 | 0 |  | 224.9 | 0 |  | 482 | 0 |  | n | 0
2018-05-21 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-21 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 182 | 1218 | 1400 |  | 0 | 0 | 0 |  | 535.2 | 0 |  | 182 | 0 |  | n | 0
2018-05-22 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 24 | 1376 | 1400 |  | 0 | 0 | 0 |  | 698.6 | 0 |  | 24 | 0 |  | n | 0
2018-05-22 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-22 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 16.1 |  | n | 0
2018-05-23 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 25 |  | n | 0
2018-05-23 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 50 |  | n | 0
2018-05-23 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-23 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 15 | 1385 | 1400 |  | 0 | 0 | 0 |  | 707.7 | 0 |  | 15 | 0 |  | n | 0
2018-05-24 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 218 | 1182 | 1400 |  | 0 | 0 | 0 |  | 497.7 | 0 |  | 60 | 0 |  | n | 0
2018-05-24 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 404 | 996 | 1400 |  | 0 | 0 | 0 |  | 305.2 | 0 |  | 18.5 | 0 |  | n | 0
2018-05-24 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 91 | 1309 | 1400 |  | 0 | 0 | 0 |  | 629 | 0 |  | 0 | 79.2 |  | n | 0
2018-05-24 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 97 | 1303 | 1400 |  | 0 | 0 | 0 |  | 622.8 | 0 |  | 0 | 131.4 |  | n | 0
2018-05-24 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-24 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 205 | 1195 | 1400 |  | 0 | 0 | 0 |  | 511.2 | 0 |  | 205 | 0 |  | n | 0
2018-05-25 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-25 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-26 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 436 | 964 | 1400 |  | 0 | 0 | 0 |  | 273.1 | 0 |  | 92.1 | 0 |  | n | 0
2018-05-26 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-26 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 86 |  | n | 0
2018-05-26 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 55 |  | n | 0
2018-05-26 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 85 |  | n | 0
2018-05-26 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 81 | 1319 | 1400 |  | 0 | 0 | 0 |  | 639.7 | 0 |  | 0 | 75 |  | n | 0
2018-05-26 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 155 | 1245 | 1400 |  | 0 | 0 | 0 |  | 562.8 | 0 |  | 0 | 203.7 |  | n | 0
2018-05-26 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 171.5 |  | n | 0
2018-05-26 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-26 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 26 |  | n | 0
2018-05-26 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 218 | 1182 | 1400 |  | 0 | 0 | 0 |  | 497.4 | 0 |  | 147.6 | 0 |  | n | 0
2018-05-26 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 308 | 1092 | 1400 |  | 0 | 0 | 0 |  | 404.4 | 0 |  | 308 | 0 |  | n | 0
2018-05-26 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 173 | 173 |  | 0 | 0 | 0 |  | 179.1 | 0 |  | 35.3 | 0 |  | n | 0
2018-05-26 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 22 | 22 |  | 0 | 0 | 0 |  | 22.2 | 0 |  | 0 | 12 |  | n | 0
2018-05-26 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 14 | 0 | 14 |  | 0 | 0 | 0 |  | 0 | 14.6 |  | 0 | 20 |  | n | 0
2018-05-26 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 34 | 34 |  | 0 | 0 | 0 |  | 35.1 | 0 |  | 0 | 0 |  | n | 0
2018-05-26 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 199 | 199 |  | 0 | 0 | 0 |  | 205.1 | 0 |  | 0 | 0 |  | n | 0
2018-05-26 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 495 | 0 |  | 0 | 0 |  | n | 0
2018-05-26 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-26 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-26 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-26 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-26 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-26 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-27 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 600 | 600 | 1200 |  | 700 | 700 | 700 |  | 0 | 0 | 6 | 0 | 0 |  | j | 600 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Capacity on the ID market manually adjusted.
2018-05-27 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 132.9 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 171 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 217.1 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 289 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 278.4 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 507 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 651.1 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 216.1 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 143.5 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 409 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 522.8 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 481.3 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 402.7 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 347.8 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 0 | 135.2 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 48.9 | 0 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 479.2 | 0 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 542.8 | 0 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 419 | 0 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 293 | 0 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 520.9 | 0 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 700 | 0 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-27 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/8836d705-06d8-4bfc-9fb3-9d3bc556de84/2 | 0 | 0 | 0 | 700 | 700 | 1400 |  | 700 | 0 | 700 |  | 0 | 0 |  | 700 | 0 |  | n | 0 | Initially not available until 27/05/2018 23:59 (UMM 26/05/2018 09:35) due to failure on the NorNed cable on the norwegian side. Subsequently event stop updated to 26/05/2018 23:59 (UMM 26/05/2018 17:21). Therefore capacity already included in the availability overview for the ID market of the next day.
2018-05-28 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 101 | 1299 | 1400 |  | 0 | 0 | 0 |  | 619 | 0 |  | 101 | 0 |  | n | 0
2018-05-28 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 40 |  | n | 0
2018-05-28 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 48.5 |  | n | 0
2018-05-28 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 11.5 |  | n | 0
2018-05-28 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-28 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 20.7 |  | n | 0
2018-05-29 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 104.5 |  | n | 0
2018-05-29 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 60 |  | n | 0
2018-05-29 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 109 |  | n | 0
2018-05-29 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 13 |  | n | 0
2018-05-29 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-29 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 40 |  | n | 0
2018-05-30 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-30 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 421 | 979 | 1400 |  | 0 | 0 | 0 |  | 288.1 | 0 |  | 0 | 19.7 |  | n | 0
2018-05-31 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 167 |  | n | 0
2018-05-31 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 61 |  | n | 0
2018-05-31 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 61.5 |  | n | 0
2018-05-31 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-05-31 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 134.5 |  | n | 0
2018-06-01 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 127.8 |  | n | 0
2018-06-01 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 10 |  | n | 0
2018-06-01 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-01 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  | 125 | 0 |  | n | 0
2018-06-02 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  | 6.5 | 0 |  | n | 0
2018-06-02 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 235.3 | 0 |  | 50 | 0 |  | n | 0
2018-06-02 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 9 |  | n | 0
2018-06-02 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 56 |  | n | 0
2018-06-02 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 215.8 | 0 |  | 0 | 78.7 |  | n | 0
2018-06-02 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 208.4 | 0 |  | 0 | 27.5 |  | n | 0
2018-06-02 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-02 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-03 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 702.1 | 0 |  | 20 | 0 |  | n | 0
2018-06-03 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 36.5 |  | n | 0
2018-06-03 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 76.5 |  | n | 0
2018-06-03 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 6.5 |  | n | 0
2018-06-03 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-03 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 11.2 |  | n | 0
2018-06-03 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 59 |  | n | 0
2018-06-03 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 146.8 | 0 |  | 0 | 86.5 |  | n | 0
2018-06-03 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 109.1 | 0 |  | 0 | 102 |  | n | 0
2018-06-03 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 336.7 |  | 0 | 193.9 |  | n | 0
2018-06-03 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 72.2 |  | 0 | 54.2 |  | n | 0
2018-06-03 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 4.4 |  | 0 | 1.5 |  | n | 0
2018-06-03 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 614.6 | 0 |  | 0 | 236 |  | n | 0
2018-06-03 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 396 |  | n | 0
2018-06-03 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 20 |  | n | 0
2018-06-03 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 13 |  | n | 0
2018-06-03 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 19.2 |  | 0 | 120.8 |  | n | 0
2018-06-03 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 270.4 | 0 |  | 0 | 0 |  | n | 0
2018-06-03 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-03 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-03 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-03 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-03 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-03 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-04 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 269 | 1131 | 1400 |  | 0 | 0 | 0 |  | 445.6 | 0 |  | 169.5 | 0 |  | n | 0
2018-06-05 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 155.6 | 0 |  | n | 0
2018-06-05 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 570 | 830 | 1400 |  | 0 | 0 | 0 |  | 134.2 | 0 |  | 0 | 192.3 |  | n | 0
2018-06-05 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 59.4 |  | n | 0
2018-06-05 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 416 | 984 | 1400 |  | 0 | 0 | 0 |  | 293.3 | 0 |  | 0 | 68.6 |  | n | 0
2018-06-05 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 333.3 |  | n | 0
2018-06-05 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 263.6 |  | n | 0
2018-06-05 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 570 |  | n | 0
2018-06-05 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-05 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 1.5 |  | n | 0
2018-06-06 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 109.5 |  | n | 0
2018-06-06 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 1.5 |  | n | 0
2018-06-06 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 101 | 1299 | 1400 |  | 0 | 0 | 0 |  | 619 | 0 |  | 0 | 205 |  | n | 0
2018-06-06 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 122 |  | n | 0
2018-06-06 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 47.5 |  | n | 0
2018-06-06 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 77.2 |  | n | 0
2018-06-06 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 42.9 |  | n | 0
2018-06-06 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 93.4 |  | n | 0
2018-06-06 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-06 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 350.4 | 0 |  | n | 0
2018-06-07 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 39.5 | 0 |  | n | 0
2018-06-07 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 870 | 530 | 1400 |  | 0 | 0 | 0 |  | 0 | 176 |  | 106.5 | 0 |  | n | 0
2018-06-07 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 622 | 778 | 1400 |  | 0 | 0 | 0 |  | 80.2 | 0 |  | 88 | 0 |  | n | 0
2018-06-07 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 99.2 | 0 |  | n | 0
2018-06-07 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 926 | 474 | 1400 |  | 0 | 0 | 0 |  | 0 | 233.3 |  | 15.6 | 0 |  | n | 0
2018-06-07 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 327 | 1073 | 1400 |  | 0 | 0 | 0 |  | 385.7 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-07 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 85 |  | n | 0
2018-06-08 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 7 | 0 |  | n | 0
2018-06-08 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 689 | 711 | 1400 |  | 0 | 0 | 0 |  | 11.1 | 0 |  | 0 | 1.5 |  | n | 0
2018-06-08 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 90 | 1310 | 1400 |  | 0 | 0 | 0 |  | 630.1 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 1.5 |  | n | 0
2018-06-08 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 9 | 1391 | 1400 |  | 0 | 0 | 0 |  | 714.2 | 0 |  | 9 | 0 |  | n | 0
2018-06-08 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-08 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 119 | 1281 | 1400 |  | 0 | 0 | 0 |  | 600.4 | 0 |  | 119 | 0 |  | n | 0
2018-06-08 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 165 | 1235 | 1400 |  | 0 | 0 | 0 |  | 553 | 0 |  | 165 | 0 |  | n | 0
2018-06-08 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 91 | 1309 | 1400 |  | 0 | 0 | 0 |  | 628.9 | 0 |  | 91 | 0 |  | n | 0
2018-06-09 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 409 | 991 | 1400 |  | 0 | 0 | 0 |  | 300.5 | 0 |  | 0 | 117.6 |  | n | 0
2018-06-09 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 866 | 534 | 1400 |  | 0 | 0 | 0 |  | 0 | 171 |  | 0 | 233 |  | n | 0
2018-06-09 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 391.8 |  | n | 0
2018-06-09 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 492 | 908 | 1400 |  | 0 | 0 | 0 |  | 214.5 | 0 |  | 0 | 327.3 |  | n | 0
2018-06-09 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 545 | 855 | 1400 |  | 0 | 0 | 0 |  | 160.4 | 0 |  | 0 | 314.4 |  | n | 0
2018-06-09 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 164.3 |  | n | 0
2018-06-09 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 599 | 801 | 1400 |  | 0 | 0 | 0 |  | 104 | 0 |  | 0 | 24.1 |  | n | 0
2018-06-09 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 115.1 |  | n | 0
2018-06-09 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 10 |  | n | 0
2018-06-09 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 125 |  | n | 0
2018-06-09 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 210.9 |  | n | 0
2018-06-09 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 165 | 1235 | 1400 |  | 0 | 0 | 0 |  | 552.4 | 0 |  | 0 | 164.9 |  | n | 0
2018-06-09 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 542 | 858 | 1400 |  | 0 | 0 | 0 |  | 163.5 | 0 |  | 0 | 70 |  | n | 0
2018-06-09 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 888 | 512 | 1400 |  | 0 | 0 | 0 |  | 0 | 194.5 |  | 0 | 56 |  | n | 0
2018-06-09 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 1147 | 253 | 1400 |  | 0 | 0 | 0 |  | 0 | 462 |  | 0 | 145 |  | n | 0
2018-06-09 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 1190 | 210 | 1400 |  | 0 | 0 | 0 |  | 0 | 506.5 |  | 0 | 80 |  | n | 0
2018-06-09 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 811 | 589 | 1400 |  | 0 | 0 | 0 |  | 0 | 114.4 |  | 0 | 65 |  | n | 0
2018-06-09 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 212 | 1188 | 1400 |  | 0 | 0 | 0 |  | 504.6 | 0 |  | 0 | 63.5 |  | n | 0
2018-06-09 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-09 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-09 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-09 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-09 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-09 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 310 | 1090 | 1400 |  | 0 | 0 | 0 |  | 402.6 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 42 | 1358 | 1400 |  | 0 | 0 | 0 |  | 679.4 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 196 | 1204 | 1400 |  | 0 | 0 | 0 |  | 520.5 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 307 | 1093 | 1400 |  | 0 | 0 | 0 |  | 405.9 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 459 | 941 | 1400 |  | 0 | 0 | 0 |  | 249.2 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 700 | 700 | 1400 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 1191 | 209 | 1400 |  | 0 | 0 | 0 |  | 0 | 507.3 |  | 0 | 78.4 |  | n | 0
2018-06-10 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 823 | 577 | 1400 |  | 0 | 0 | 0 |  | 0 | 127.3 |  | 0 | 70 |  | n | 0
2018-06-10 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 687 | 713 | 1400 |  | 0 | 0 | 0 |  | 13 | 0 |  | 0 | 90 |  | n | 0
2018-06-10 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 502 | 898 | 1400 |  | 0 | 0 | 0 |  | 204.6 | 0 |  | 0 | 70 |  | n | 0
2018-06-10 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 763 | 637 | 1400 |  | 0 | 0 | 0 |  | 0 | 64.7 |  | 0 | 10.2 |  | n | 0
2018-06-10 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 1362 | 38 | 1400 |  | 0 | 0 | 0 |  | 0 | 683.7 |  | 0 | 11.7 |  | n | 0
2018-06-10 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-06-10 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 1400 | 0 | 1400 |  | 0 | 0 | 0 |  | 0 | 723 |  | 0 | 0 |  | n | 0
2018-06-10 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 911 | 489 | 1400 |  | 0 | 0 | 0 |  | 0 | 217.6 |  | 0 | 0.5 |  | n | 0
2018-06-10 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 311 | 1089 | 1400 |  | 0 | 0 | 0 |  | 401.4 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-10 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 433 | 967 | 1400 |  | 0 | 0 | 0 |  | 276.1 | 0 |  | 0 | 72.8 |  | n | 0
2018-06-11 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 44 | 1356 | 1400 |  | 0 | 0 | 0 |  | 677.8 | 0 |  | 0 | 102.8 |  | n | 0
2018-06-11 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 8.8 |  | n | 0
2018-06-11 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 1400 | 1400 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-11 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 68 | 1332 | 1400 |  | 0 | 0 | 0 |  | 652.6 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 00 - 01 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 33.6 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 01 - 02 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 02 - 03 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 03 - 04 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 04 - 05 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 05 - 06 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 137.1 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 06 - 07 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 07 - 08 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 08 - 09 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 09 - 10 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 10 - 11 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 11 - 12 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 12 - 13 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 13 - 14 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 14 - 15 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 15 - 16 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 16 - 17 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 17 - 18 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 18 - 19 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 19 - 20 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 20 - 21 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 21 - 22 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 247.8 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 22 - 23 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 627.4 | 0 |  | 0 | 0 |  | n | 0
2018-06-12 | 23 - 00 | n | n |  | 723 | 723 | 1446 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 8.4 | 0 |  | 0 | 0 |  | n | 0
2018-06-13 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 610.6 |  |  |  |  | n | 0
2018-06-13 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-13 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-13 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-13 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-13 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 619 |  |  |  |  | n | 0
2018-06-13 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-13 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-06-13 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-13 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-13 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-13 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-13 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-13 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-13 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 584.4 | 0 |  |  |  |  | n | 0
2018-06-13 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 476 | 0 |  |  |  |  | n | 0
2018-06-13 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-13 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 466.5 | 0 |  |  |  |  | n | 0
2018-06-13 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-13 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-13 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-13 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-13 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-13 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-14 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-06-14 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-14 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-14 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 158.9 |  |  |  |  | n | 0
2018-06-14 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-14 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-06-14 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-14 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-14 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-14 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-14 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-14 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 593.4 | 0 |  |  |  |  | n | 0
2018-06-15 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-15 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 503.9 | 0 |  |  |  |  | n | 0
2018-06-15 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-15 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-16 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 138.8 | 0 |  |  |  |  | n | 0
2018-06-16 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 267.6 | 0 |  |  |  |  | n | 0
2018-06-16 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 363.1 | 0 |  |  |  |  | n | 0
2018-06-16 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 168.2 | 0 |  |  |  |  | n | 0
2018-06-16 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 224.9 | 0 |  |  |  |  | n | 0
2018-06-16 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 172.2 | 0 |  |  |  |  | n | 0
2018-06-16 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-16 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-16 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 37.2 | 0 |  |  |  |  | n | 0
2018-06-16 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-16 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 13.2 |  |  |  |  | n | 0
2018-06-16 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 82.6 |  |  |  |  | n | 0
2018-06-16 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 79.1 |  |  |  |  | n | 0
2018-06-16 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 548.7 |  |  |  |  | n | 0
2018-06-16 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 314.2 |  |  |  |  | n | 0
2018-06-16 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 416.4 |  |  |  |  | n | 0
2018-06-16 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 267.5 |  |  |  |  | n | 0
2018-06-16 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 416.1 |  |  |  |  | n | 0
2018-06-16 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 202.9 | 0 |  |  |  |  | n | 0
2018-06-16 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-16 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 186.2 | 0 |  |  |  |  | n | 0
2018-06-16 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 381.5 | 0 |  |  |  |  | n | 0
2018-06-16 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 670.7 | 0 |  |  |  |  | n | 0
2018-06-16 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-17 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-17 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-06-17 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-17 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 398.6 |  |  |  |  | n | 0
2018-06-17 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 72 |  |  |  |  | n | 0
2018-06-17 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 547 | 0 |  |  |  |  | n | 0
2018-06-17 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-17 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-17 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-17 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 166.4 | 0 |  |  |  |  | n | 0
2018-06-18 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 629.3 | 0 |  |  |  |  | n | 0
2018-06-18 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 10.3 | 0 |  |  |  |  | n | 0
2018-06-18 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 294.3 |  |  |  |  | n | 0
2018-06-18 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 206.9 |  |  |  |  | n | 0
2018-06-18 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 147.9 |  |  |  |  | n | 0
2018-06-18 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-06-18 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-18 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-18 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 319.8 | 0 |  |  |  |  | n | 0
2018-06-19 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 495.5 | 0 |  |  |  |  | n | 0
2018-06-19 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 364.6 | 0 |  |  |  |  | n | 0
2018-06-19 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 362 | 0 |  |  |  |  | n | 0
2018-06-19 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 642.1 | 0 |  |  |  |  | n | 0
2018-06-19 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 532.2 | 0 |  |  |  |  | n | 0
2018-06-19 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-19 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-20 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 274.2 | 0 |  |  |  |  | n | 0
2018-06-20 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 685.5 | 0 |  |  |  |  | n | 0
2018-06-20 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 660.3 | 0 |  |  |  |  | n | 0
2018-06-20 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-20 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 423.3 | 0 |  |  |  |  | n | 0
2018-06-21 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 630.3 | 0 |  |  |  |  | n | 0
2018-06-21 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 101.2 | 0 |  |  |  |  | n | 0
2018-06-21 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-21 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-06-21 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-21 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 613.8 | 0 |  |  |  |  | n | 0
2018-06-21 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 500.6 | 0 |  |  |  |  | n | 0
2018-06-21 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 691 | 0 |  |  |  |  | n | 0
2018-06-21 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 438.5 | 0 |  |  |  |  | n | 0
2018-06-21 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-21 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-22 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 187.4 |  |  |  |  | n | 0
2018-06-22 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 225.4 |  |  |  |  | n | 0
2018-06-22 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 276.5 |  |  |  |  | n | 0
2018-06-22 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 422 |  |  |  |  | n | 0
2018-06-22 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 611.2 |  |  |  |  | n | 0
2018-06-22 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 14.9 |  |  |  |  | n | 0
2018-06-22 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-22 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 628.6 | 0 |  |  |  |  | n | 0
2018-06-22 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 517 | 0 |  |  |  |  | n | 0
2018-06-22 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 248.5 | 0 |  |  |  |  | n | 0
2018-06-22 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-22 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-23 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 225.1 | 0 |  |  |  |  | n | 0
2018-06-23 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 83.3 |  |  |  |  | n | 0
2018-06-23 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-23 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 295.6 |  |  |  |  | n | 0
2018-06-23 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 514.9 |  |  |  |  | n | 0
2018-06-23 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 510.5 |  |  |  |  | n | 0
2018-06-23 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 445 |  |  |  |  | n | 0
2018-06-23 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 358.6 |  |  |  |  | n | 0
2018-06-23 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 95 |  |  |  |  | n | 0
2018-06-23 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 264.7 | 0 |  |  |  |  | n | 0
2018-06-23 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-23 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-23 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-23 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-23 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-23 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 702.9 | 0 |  |  |  |  | n | 0
2018-06-23 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 323.5 | 0 |  |  |  |  | n | 0
2018-06-23 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 444.6 | 0 |  |  |  |  | n | 0
2018-06-23 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 263 | 0 |  |  |  |  | n | 0
2018-06-23 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 564.2 | 0 |  |  |  |  | n | 0
2018-06-23 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 722.2 | 0 |  |  |  |  | n | 0
2018-06-23 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 622 | 0 |  |  |  |  | n | 0
2018-06-23 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-23 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-24 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 220 | 0 |  |  |  |  | n | 0
2018-06-24 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-24 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 199.5 |  |  |  |  | n | 0
2018-06-24 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 370.8 |  |  |  |  | n | 0
2018-06-24 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 431.2 |  |  |  |  | n | 0
2018-06-24 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 610.7 |  |  |  |  | n | 0
2018-06-24 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-24 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-24 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-24 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-24 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 650.1 |  |  |  |  | n | 0
2018-06-24 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 196.5 |  |  |  |  | n | 0
2018-06-24 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 282.6 |  |  |  |  | n | 0
2018-06-24 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 345.6 |  |  |  |  | n | 0
2018-06-24 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 114.8 | 0 |  |  |  |  | n | 0
2018-06-24 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 504.2 |  |  |  |  | n | 0
2018-06-24 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 344.3 |  |  |  |  | n | 0
2018-06-24 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 175.9 |  |  |  |  | n | 0
2018-06-24 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-24 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-24 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-24 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-24 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-24 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 445.3 | 0 |  |  |  |  | n | 0
2018-06-25 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 446 | 0 |  |  |  |  | n | 0
2018-06-25 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 607 | 0 |  |  |  |  | n | 0
2018-06-25 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 305.4 | 0 |  |  |  |  | n | 0
2018-06-25 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 347.9 | 0 |  |  |  |  | n | 0
2018-06-25 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 371.3 | 0 |  |  |  |  | n | 0
2018-06-25 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 479.9 | 0 |  |  |  |  | n | 0
2018-06-25 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 709 | 0 |  |  |  |  | n | 0
2018-06-25 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 546.1 | 0 |  |  |  |  | n | 0
2018-06-25 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 502.4 | 0 |  |  |  |  | n | 0
2018-06-25 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-25 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-26 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-26 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 98 | 0 |  |  |  |  | n | 0
2018-06-26 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 348.2 | 0 |  |  |  |  | n | 0
2018-06-26 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 428.1 | 0 |  |  |  |  | n | 0
2018-06-26 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 388.1 | 0 |  |  |  |  | n | 0
2018-06-26 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 722.8 | 0 |  |  |  |  | n | 0
2018-06-26 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 269.6 | 0 |  |  |  |  | n | 0
2018-06-26 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-26 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-27 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-27 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-27 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-27 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-27 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-27 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-27 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-28 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-06-28 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 643 |  |  |  |  | n | 0
2018-06-28 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-28 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 589.4 |  |  |  |  | n | 0
2018-06-28 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-28 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-06-28 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 154.2 | 0 |  |  |  |  | n | 0
2018-06-28 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-28 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-28 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 346.9 | 0 |  |  |  |  | n | 0
2018-06-28 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 575.1 | 0 |  |  |  |  | n | 0
2018-06-28 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 642.1 | 0 |  |  |  |  | n | 0
2018-06-29 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 23.1 | 0 |  |  |  |  | n | 0
2018-06-29 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-29 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-29 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-29 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 143 |  |  |  |  | n | 0
2018-06-29 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-06-29 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-06-29 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 556.1 | 0 |  |  |  |  | n | 0
2018-06-29 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 638.2 | 0 |  |  |  |  | n | 0
2018-06-29 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 563.4 | 0 |  |  |  |  | n | 0
2018-06-29 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-29 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-06-30 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 443.6 | 0 |  |  |  |  | n | 0
2018-06-30 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 79.5 | 0 |  |  |  |  | n | 0
2018-06-30 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 147.2 | 0 |  |  |  |  | n | 0
2018-06-30 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 47.4 |  |  |  |  | n | 0
2018-06-30 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 230.2 |  |  |  |  | n | 0
2018-06-30 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 519.7 |  |  |  |  | n | 0
2018-06-30 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 558.9 |  |  |  |  | n | 0
2018-06-30 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-30 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-30 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 191.8 | 0 |  |  |  |  | n | 0
2018-06-30 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 673.1 | 0 |  |  |  |  | n | 0
2018-06-30 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 475 | 0 |  |  |  |  | n | 0
2018-06-30 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 291.4 | 0 |  |  |  |  | n | 0
2018-06-30 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 4.6 |  |  |  |  | n | 0
2018-06-30 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 193.2 |  |  |  |  | n | 0
2018-06-30 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 522.1 |  |  |  |  | n | 0
2018-06-30 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-06-30 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 104 |  |  |  |  | n | 0
2018-06-30 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 140.2 | 0 |  |  |  |  | n | 0
2018-06-30 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 630 | 0 |  |  |  |  | n | 0
2018-06-30 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 367.6 | 0 |  |  |  |  | n | 0
2018-06-30 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-06-30 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 615 | 0 |  |  |  |  | n | 0
2018-06-30 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 711.8 | 0 |  |  |  |  | n | 0
2018-07-01 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 92.8 | 0 |  |  |  |  | n | 0
2018-07-01 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 526.2 |  |  |  |  | n | 0
2018-07-01 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-01 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 643.6 |  |  |  |  | n | 0
2018-07-01 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 297.9 |  |  |  |  | n | 0
2018-07-01 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-07-01 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 220.2 | 0 |  |  |  |  | n | 0
2018-07-01 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 145.8 | 0 |  |  |  |  | n | 0
2018-07-01 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-01 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-07-02 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-07-02 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-02 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-02 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-02 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-02 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 104 |  |  |  |  | n | 0
2018-07-02 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 515 | 0 |  |  |  |  | n | 0
2018-07-02 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-02 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 569.8 | 0 |  |  |  |  | n | 0
2018-07-03 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 49.2 |  |  |  |  | n | 0
2018-07-03 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 668.2 |  |  |  |  | n | 0
2018-07-03 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-03 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-03 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-07-03 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-07-03 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-07-03 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-03 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-07-04 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 460.2 |  |  |  |  | n | 0
2018-07-04 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 180.1 |  |  |  |  | n | 0
2018-07-04 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-07-04 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 230.3 |  |  |  |  | n | 0
2018-07-04 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 310 |  |  |  |  | n | 0
2018-07-04 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-07-04 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-04 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-07-05 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 191.5 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 427.5 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 190.8 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-05 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 308.8 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-06 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 277.4 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 414.9 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-07 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-07 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 203.7 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-07 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-07 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-07 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-07 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-07 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-07 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-07 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-07 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-07 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-07 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 85.8 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-08 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-08 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-08 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-08 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-08 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-08 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-08 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-08 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-08 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-08 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/d28512df-1bdf-420c-9036-bd93bb3602a4/1 | 0 | 433 | 433 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 433 |  |  |  |  | n | 0 | TenneT will perform required maintenance in Eemshaven substation.This results in a reduction of the capacity NO2->NL. The reduction is on both days from 07:00 – 18:00.
2018-07-08 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-08 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 289.7 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 78.6 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 267.1 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 320.7 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 335.8 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 145.5 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 147.6 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-09 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-10 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 306.9 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-11 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 169.9 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-12 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 216.9 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 6.4 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 135.3 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 137.1 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 71.7 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 148.1 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 382.1 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 83.9 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-13 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 61.8 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 5 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 119.3 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 245.9 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 216.3 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 208.5 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 99.2 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 307.9 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 428.9 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-14 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 260.7 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 241.5 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 333.8 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 211 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-15 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 140.3 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 368.4 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-16 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 200.4 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 134.8 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-17 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 225.8 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 72.3 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 195.3 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 86.9 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 430.8 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 263.5 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 32.6 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-18 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 76.1 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 165.2 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 185.5 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-19 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 369.2 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 355 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-20 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 391.9 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 61.8 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-21 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 359.3 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 186 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 200.9 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-22 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 430.4 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 14.8 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 397.7 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 95.8 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-23 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 27.5 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 261.2 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-24 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 244.5 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 83.8 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 55.9 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 78.6 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-25 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 32.2 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 314.9 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 320.2 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 336.8 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 179.2 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-26 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 400.7 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 218.3 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-27 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 315.6 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 126.5 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 54.8 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 61.7 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 27.7 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 70 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 69.9 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 389.2 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-28 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 194 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-29 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 158.5 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0.2 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 273.1 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 347.5 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-30 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-07-31 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 330 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 330 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 330 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 330 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 330 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 330 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 330 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-07-31 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 330 | 330 | 660 |  |  | 0 |  | 380 | 380 | 380 |  | 0 | 0 |  |  |  |  | j | 100 | Failure in substation in Netherlands. Additional limited capacity due to restrictions in the Norwegian grid, refer to the following UMM: https://umm.nordpoolgroup.com/#/messages/430b5ea2-8a77-4b91-9a93-08cf3bf2dc45/9. Therefore the additional restriction has been adjusted in column X.
2018-08-01 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 327.7 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 291.3 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-01 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-02 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-03 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-04 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 7.7 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 433 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 353.7 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 247.1 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 165.8 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 328.4 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 220.3 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-05 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-06 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-07 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 77.7 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 336.2 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 412.3 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-08 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 420.8 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 433 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 0 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-09 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/26d8cd7c-da95-4d35-b08a-be635623140f/9 | 433 | 433 | 866 |  |  | 0 |  | 281 | 281 | 281 |  | 0 | 193.1 |  |  |  |  | n | 0 | Failure in substation in Netherlands.
2018-08-10 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 163.8 |  |  |  |  | n | 0
2018-08-10 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 222.6 | 0 |  |  |  |  | n | 0
2018-08-10 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-10 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 154.4 |  |  |  |  | n | 0
2018-08-10 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 23.7 | 0 |  |  |  |  | n | 0
2018-08-10 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 307 | 0 |  |  |  |  | n | 0
2018-08-10 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 156.1 | 0 |  |  |  |  | n | 0
2018-08-10 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 178.9 | 0 |  |  |  |  | n | 0
2018-08-10 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-10 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 586.2 | 0 |  |  |  |  | n | 0
2018-08-10 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 56.2 | 0 |  |  |  |  | n | 0
2018-08-10 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-10 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-10 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-10 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-10 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 164.6 |  |  |  |  | n | 0
2018-08-10 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-10 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 513 | 0 |  |  |  |  | n | 0
2018-08-10 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-10 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-10 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-10 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-10 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-10 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-11 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-11 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-11 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-11 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-11 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-11 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-11 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-11 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-11 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-11 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 104 |  |  |  |  | n | 0
2018-08-11 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-11 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 514.4 |  |  |  |  | n | 0
2018-08-11 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-11 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 174.9 |  |  |  |  | n | 0
2018-08-11 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-11 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 693.7 |  |  |  |  | n | 0
2018-08-11 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 74.7 |  |  |  |  | n | 0
2018-08-11 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 544.3 | 0 |  |  |  |  | n | 0
2018-08-11 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 528.7 | 0 |  |  |  |  | n | 0
2018-08-11 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-11 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-11 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-11 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-11 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-12 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-12 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-12 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-12 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-12 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-12 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-12 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-12 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-12 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 104 |  |  |  |  | n | 0
2018-08-12 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-12 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-12 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-12 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-12 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-12 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-12 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-12 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 646.6 |  |  |  |  | n | 0
2018-08-12 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-08-12 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-12 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-12 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-12 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-12 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-12 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-13 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-13 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-13 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-13 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-13 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-13 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-13 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-14 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-14 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-14 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-14 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-14 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-14 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-14 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-08-14 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-14 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-14 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-14 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-14 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-14 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-14 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-14 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-08-14 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 542.5 |  |  |  |  | n | 0
2018-08-14 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-08-14 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-14 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-14 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-14 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-14 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-14 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-14 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-15 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-15 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-15 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-15 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-15 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-15 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-15 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-15 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-15 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-15 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-15 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-15 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-15 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 301.1 | 0 |  |  |  |  | n | 0
2018-08-15 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 186.8 | 0 |  |  |  |  | n | 0
2018-08-15 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 238.3 |  |  |  |  | n | 0
2018-08-15 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-15 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 294.9 |  |  |  |  | n | 0
2018-08-15 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 324.1 | 0 |  |  |  |  | n | 0
2018-08-15 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-15 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-15 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-15 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-15 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-15 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-16 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-16 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-16 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-16 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-16 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-16 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 630.7 | 0 |  |  |  |  | n | 0
2018-08-16 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 506.2 | 0 |  |  |  |  | n | 0
2018-08-16 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-16 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 251.8 | 0 |  |  |  |  | n | 0
2018-08-16 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-16 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 398.4 | 0 |  |  |  |  | n | 0
2018-08-17 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-17 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-17 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-17 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-17 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-17 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-17 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 510 | 0 |  |  |  |  | n | 0
2018-08-18 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-18 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-18 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-18 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-18 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-18 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-18 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-19 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-19 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-19 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-19 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-19 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 686.6 | 0 |  |  |  |  | n | 0
2018-08-19 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 552.9 | 0 |  |  |  |  | n | 0
2018-08-19 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-19 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-19 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-19 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-19 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-19 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-19 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-19 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 222 | 0 |  |  |  |  | n | 0
2018-08-19 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 134.5 | 0 |  |  |  |  | n | 0
2018-08-19 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-19 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-19 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-19 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-19 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-19 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-19 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-19 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-19 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 336.2 | 0 |  |  |  |  | n | 0
2018-08-20 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-20 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-20 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-20 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-20 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-20 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-21 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-22 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-22 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 493.4 | 0 |  |  |  |  | n | 0
2018-08-23 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 262.7 | 0 |  |  |  |  | n | 0
2018-08-23 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 139.6 | 0 |  |  |  |  | n | 0
2018-08-23 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 83 | 0 |  |  |  |  | n | 0
2018-08-23 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 620.5 | 0 |  |  |  |  | n | 0
2018-08-23 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 511.9 | 0 |  |  |  |  | n | 0
2018-08-23 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 664.7 | 0 |  |  |  |  | n | 0
2018-08-23 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-23 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 368.2 | 0 |  |  |  |  | n | 0
2018-08-24 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-24 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-24 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-24 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 625.8 | 0 |  |  |  |  | n | 0
2018-08-24 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 6.8 | 0 |  |  |  |  | n | 0
2018-08-24 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-24 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-24 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-24 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-24 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-24 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-24 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 566.4 | 0 |  |  |  |  | n | 0
2018-08-25 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-25 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 684.8 | 0 |  |  |  |  | n | 0
2018-08-25 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 482.7 | 0 |  |  |  |  | n | 0
2018-08-25 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 464.5 | 0 |  |  |  |  | n | 0
2018-08-25 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 476.3 | 0 |  |  |  |  | n | 0
2018-08-25 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 583.5 | 0 |  |  |  |  | n | 0
2018-08-25 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-25 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-26 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 255.6 | 0 |  |  |  |  | n | 0
2018-08-26 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-26 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-26 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-26 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 621.6 | 0 |  |  |  |  | n | 0
2018-08-26 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 178.7 | 0 |  |  |  |  | n | 0
2018-08-26 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-26 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 55.5 |  |  |  |  | n | 0
2018-08-26 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-26 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-26 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 229.9 | 0 |  |  |  |  | n | 0
2018-08-26 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-26 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-26 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-26 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-08-26 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-26 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 557.8 |  |  |  |  | n | 0
2018-08-26 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 61.2 | 0 |  |  |  |  | n | 0
2018-08-26 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 680.2 | 0 |  |  |  |  | n | 0
2018-08-26 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-26 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-26 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-26 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-26 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-27 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-08-27 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 595.7 |  |  |  |  | n | 0
2018-08-27 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-27 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-08-27 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 226.5 |  |  |  |  | n | 0
2018-08-27 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 79.6 | 0 |  |  |  |  | n | 0
2018-08-27 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 698.6 | 0 |  |  |  |  | n | 0
2018-08-27 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-27 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-27 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-27 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-27 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-27 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 716.8 | 0 |  |  |  |  | n | 0
2018-08-27 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-27 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-27 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 508.5 | 0 |  |  |  |  | n | 0
2018-08-27 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 252.3 | 0 |  |  |  |  | n | 0
2018-08-27 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 410.4 | 0 |  |  |  |  | n | 0
2018-08-27 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-27 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-27 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-27 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-27 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 704.9 | 0 |  |  |  |  | n | 0
2018-08-27 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 567.4 | 0 |  |  |  |  | n | 0
2018-08-28 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 372.5 | 0 |  |  |  |  | n | 0
2018-08-28 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 351.8 | 0 |  |  |  |  | n | 0
2018-08-28 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-28 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-28 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 700.4 | 0 |  |  |  |  | n | 0
2018-08-29 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 435.6 | 0 |  |  |  |  | n | 0
2018-08-29 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-29 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-29 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-29 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-29 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-08-29 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-29 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 168.4 | 0 |  |  |  |  | n | 0
2018-08-29 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 647.3 | 0 |  |  |  |  | n | 0
2018-08-30 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 130.5 | 0 |  |  |  |  | n | 0
2018-08-30 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-30 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-30 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 374.3 |  |  |  |  | n | 0
2018-08-30 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 64.1 |  |  |  |  | n | 0
2018-08-30 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-30 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-30 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 60.5 | 0 |  |  |  |  | n | 0
2018-08-30 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 662.9 | 0 |  |  |  |  | n | 0
2018-08-30 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 530.1 | 0 |  |  |  |  | n | 0
2018-08-30 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 263.8 | 0 |  |  |  |  | n | 0
2018-08-30 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 85.2 | 0 |  |  |  |  | n | 0
2018-08-30 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 24.8 |  |  |  |  | n | 0
2018-08-30 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 69.1 | 0 |  |  |  |  | n | 0
2018-08-30 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 126.4 | 0 |  |  |  |  | n | 0
2018-08-30 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 241.3 | 0 |  |  |  |  | n | 0
2018-08-30 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 411.6 | 0 |  |  |  |  | n | 0
2018-08-30 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-30 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-30 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-30 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-30 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-30 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 316.3 | 0 |  |  |  |  | n | 0
2018-08-30 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 107.2 | 0 |  |  |  |  | n | 0
2018-08-31 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-31 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-31 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-31 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-31 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-08-31 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-08-31 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 710.4 | 0 |  |  |  |  | n | 0
2018-08-31 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 720.8 | 0 |  |  |  |  | n | 0
2018-08-31 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-08-31 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 512.9 | 0 |  |  |  |  | n | 0
2018-09-01 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-01 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-01 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-01 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-01 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-01 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-01 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-01 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-01 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-09-01 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-01 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-01 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-01 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-01 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-01 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-01 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-01 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-01 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-09-01 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-01 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-01 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-01 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-01 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-01 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 690.9 | 0 |  |  |  |  | n | 0
2018-09-02 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-02 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 511.4 | 0 |  |  |  |  | n | 0
2018-09-02 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 107.6 |  |  |  |  | n | 0
2018-09-02 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 670.7 |  |  |  |  | n | 0
2018-09-02 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-09-02 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-09-02 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-09-02 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-09-02 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-09-02 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 619.9 |  |  |  |  | n | 0
2018-09-02 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 685.3 |  |  |  |  | n | 0
2018-09-02 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 441.6 |  |  |  |  | n | 0
2018-09-02 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 115.2 |  |  |  |  | n | 0
2018-09-02 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-09-02 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-09-02 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-09-02 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 243.2 |  |  |  |  | n | 0
2018-09-02 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 358.4 |  |  |  |  | n | 0
2018-09-02 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 260.6 | 0 |  |  |  |  | n | 0
2018-09-02 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-02 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-02 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-02 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-02 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 440.5 | 0 |  |  |  |  | n | 0
2018-09-03 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-03 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-03 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-03 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 547.6 | 0 |  |  |  |  | n | 0
2018-09-03 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 484.7 | 0 |  |  |  |  | n | 0
2018-09-04 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-04 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-04 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-04 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 17 |  |  |  |  | n | 0
2018-09-04 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-04 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-04 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-04 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-05 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-05 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-05 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-05 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-05 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-05 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-05 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-05 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 426.9 | 0 |  |  |  |  | n | 0
2018-09-06 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-06 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-06 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-06 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-06 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-06 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-06 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-06 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 279.9 | 0 |  |  |  |  | n | 0
2018-09-07 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-07 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-07 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-07 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-07 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-07 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 405.1 | 0 |  |  |  |  | n | 0
2018-09-07 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 330 | 0 |  |  |  |  | n | 0
2018-09-07 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 361.9 | 0 |  |  |  |  | n | 0
2018-09-07 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 432 | 0 |  |  |  |  | n | 0
2018-09-07 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-07 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 698.5 | 0 |  |  |  |  | n | 0
2018-09-08 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 79.5 | 0 |  |  |  |  | n | 0
2018-09-08 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 407 | 0 |  |  |  |  | n | 0
2018-09-08 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-08 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 481.2 | 0 |  |  |  |  | n | 0
2018-09-08 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 304.6 | 0 |  |  |  |  | n | 0
2018-09-08 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 326.2 | 0 |  |  |  |  | n | 0
2018-09-08 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 713.4 | 0 |  |  |  |  | n | 0
2018-09-08 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 94.4 | 0 |  |  |  |  | n | 0
2018-09-08 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 669.4 | 0 |  |  |  |  | n | 0
2018-09-08 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-08 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-08 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-08 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 590.8 | 0 |  |  |  |  | n | 0
2018-09-08 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 654.7 | 0 |  |  |  |  | n | 0
2018-09-08 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 463.8 | 0 |  |  |  |  | n | 0
2018-09-08 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 599.3 | 0 |  |  |  |  | n | 0
2018-09-08 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-08 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-08 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-08 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-08 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-08 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-08 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-08 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-09 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 254.6 | 0 |  |  |  |  | n | 0
2018-09-09 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 268.7 | 0 |  |  |  |  | n | 0
2018-09-09 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 286.3 | 0 |  |  |  |  | n | 0
2018-09-09 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-09 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 38.4 |  |  |  |  | n | 0
2018-09-09 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 340 |  |  |  |  | n | 0
2018-09-09 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 356.6 |  |  |  |  | n | 0
2018-09-09 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 222.4 |  |  |  |  | n | 0
2018-09-09 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 77.8 |  |  |  |  | n | 0
2018-09-09 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 37.3 |  |  |  |  | n | 0
2018-09-09 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-09 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-09 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 118.1 |  |  |  |  | n | 0
2018-09-09 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 226.4 |  |  |  |  | n | 0
2018-09-09 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 310 |  |  |  |  | n | 0
2018-09-09 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-09-09 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-09-09 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-09 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-09 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-09 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-09 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-09 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-09 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 634.2 | 0 |  |  |  |  | n | 0
2018-09-10 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 15.2 | 0 |  |  |  |  | n | 0
2018-09-10 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-10 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-10 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 249.1 |  |  |  |  | n | 0
2018-09-10 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-10 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-10 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-11 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-11 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-11 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 576.4 |  |  |  |  | n | 0
2018-09-11 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 42.6 | 0 |  |  |  |  | n | 0
2018-09-11 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 661.6 | 0 |  |  |  |  | n | 0
2018-09-11 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-11 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-12 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-13 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 498.4 | 0 |  |  |  |  | n | 0
2018-09-14 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-14 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 304.5 | 0 |  |  |  |  | n | 0
2018-09-15 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-15 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 13.3 | 0 |  |  |  |  | n | 0
2018-09-15 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 433.7 | 0 |  |  |  |  | n | 0
2018-09-15 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-15 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-15 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-16 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-16 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 314.4 | 0 |  |  |  |  | n | 0
2018-09-16 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 152.4 | 0 |  |  |  |  | n | 0
2018-09-16 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-16 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 563.2 | 0 |  |  |  |  | n | 0
2018-09-16 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 414.8 | 0 |  |  |  |  | n | 0
2018-09-16 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 540.6 | 0 |  |  |  |  | n | 0
2018-09-16 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-16 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-16 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-16 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-16 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-09-16 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 438.6 | 0 |  |  |  |  | n | 0
2018-09-16 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 157 |  |  |  |  | n | 0
2018-09-16 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 624.7 |  |  |  |  | n | 0
2018-09-16 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 714.6 |  |  |  |  | n | 0
2018-09-16 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 95.6 |  |  |  |  | n | 0
2018-09-16 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 523.4 | 0 |  |  |  |  | n | 0
2018-09-16 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-16 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-16 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-16 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-16 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-16 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 274.2 | 0 |  |  |  |  | n | 0
2018-09-17 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 239.7 | 0 |  |  |  |  | n | 0
2018-09-17 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 428.6 | 0 |  |  |  |  | n | 0
2018-09-17 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 710.2 | 0 |  |  |  |  | n | 0
2018-09-17 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-17 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 117.6 | 0 |  |  |  |  | n | 0
2018-09-18 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 116.9 | 0 |  |  |  |  | n | 0
2018-09-18 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 235.4 | 0 |  |  |  |  | n | 0
2018-09-18 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 500.2 | 0 |  |  |  |  | n | 0
2018-09-18 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-18 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 460.6 | 0 |  |  |  |  | n | 0
2018-09-19 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/de861a73-90e5-42bc-8f93-14c53c579409/1 | 309 | 413 | 722 |  |  | 0 |  | 401 | 0 | 0 |  | 309 | 0 |  |  |  |  | n | 0 | Testing in the Norwegian grid
2018-09-19 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/de861a73-90e5-42bc-8f93-14c53c579409/1 | 309 | 413 | 722 |  |  | 0 |  | 401 | 0 | 0 |  | 309 | 0 |  |  |  |  | n | 0 | Testing in the Norwegian grid
2018-09-19 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-19 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 579.7 | 0 |  |  |  |  | n | 0
2018-09-20 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 669.5 | 0 |  |  |  |  | n | 0
2018-09-20 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-20 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-09-21 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-21 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-22 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 699.4 | 0 |  |  |  |  | n | 0
2018-09-23 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 658.2 | 0 |  |  |  |  | n | 0
2018-09-23 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 596.3 | 0 |  |  |  |  | n | 0
2018-09-23 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-23 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 562.6 | 0 |  |  |  |  | n | 0
2018-09-24 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-24 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-25 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-26 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-27 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-28 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-29 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-29 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-29 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-29 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-29 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-29 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-29 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 619 | 723 | 1342 |  |  | 0 |  | 100 | 100 | 100 |  | 619 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-29 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/e2534b98-7172-453f-aff4-f6fad15a8e88/2 | 619 | 723 | 1342 |  |  | 0 |  | 100 | 100 | 100 |  | 619 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-09-30 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-30 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-30 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-30 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-30 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-09-30 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-01 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 336.7 | 0 |  |  |  |  | n | 0
2018-10-02 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-02 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 653.9 | 0 |  |  |  |  | n | 0
2018-10-03 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 120.1 | 0 |  |  |  |  | n | 0
2018-10-03 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-03 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 525.4 | 0 |  |  |  |  | n | 0
2018-10-04 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-04 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-05 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 573.9 | 0 |  |  |  |  | n | 0
2018-10-06 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-06 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 119.2 | 0 |  |  |  |  | n | 0
2018-10-07 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-10-07 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-10-07 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-10-07 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-10-07 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-10-07 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-10-07 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-07 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 405.9 | 0 |  |  |  |  | n | 0
2018-10-08 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-08 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-09 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-10 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-11 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-12 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-13 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-14 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 633.7 | 0 |  |  |  |  | n | 0
2018-10-15 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-15 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-16 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-17 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-18 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-19 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 619 | 723 | 1342 |  |  | 0 |  | 100 | 100 | 100 |  | 619 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 619 | 723 | 1342 |  |  | 0 |  | 100 | 100 | 100 |  | 619 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-20 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-20 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 619 | 723 | 1342 |  |  | 0 |  | 100 | 100 | 100 |  | 619 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 0 | 723 | 723 |  |  | 0 |  | 700 | 700 | 700 |  | 0 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/dbd0cd25-c26a-4d94-82db-0a55c05ffa9a/2 | 619 | 723 | 1342 |  |  | 0 |  | 100 | 100 | 100 |  | 619 | 0 |  |  |  |  | n | 0 | TenneT will perform required maintenance in the Eemshaven region. This results in a reduction of the capacity NO2->NL.
2018-10-21 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-21 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-22 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-23 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-24 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-25 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-26 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 718.5 | 0 |  |  |  |  | n | 0
2018-10-27 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 625.7 | 0 |  |  |  |  | n | 0
2018-10-27 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 719.9 | 0 |  |  |  |  | n | 0
2018-10-27 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-27 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-28 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 329.4 | 0 |  |  |  |  | n | 0
2018-10-28 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-10-28 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 24.9 | 0 |  |  |  |  | n | 0
2018-10-28 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-10-28 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-10-28 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-10-28 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 271.4 | 0 |  |  |  |  | n | 0
2018-10-28 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 422.7 | 0 |  |  |  |  | n | 0
2018-10-28 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 638.7 | 0 |  |  |  |  | n | 0
2018-10-28 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-28 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-28 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 692.9 | 0 |  |  |  |  | n | 0
2018-10-28 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 578.9 | 0 |  |  |  |  | n | 0
2018-10-28 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 657.4 | 0 |  |  |  |  | n | 0
2018-10-28 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 623.2 | 0 |  |  |  |  | n | 0
2018-10-28 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-28 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-28 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-28 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-28 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-28 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-28 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-28 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 679.3 | 0 |  |  |  |  | n | 0
2018-10-28 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-28 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 156 | 0 |  |  |  |  | n | 0
2018-10-29 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-10-29 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 214 | 0 |  |  |  |  | n | 0
2018-10-29 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 372.7 | 0 |  |  |  |  | n | 0
2018-10-29 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 375.9 | 0 |  |  |  |  | n | 0
2018-10-29 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 465.3 | 0 |  |  |  |  | n | 0
2018-10-29 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-29 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 499 | 0 |  |  |  |  | n | 0
2018-10-30 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 440.8 | 0 |  |  |  |  | n | 0
2018-10-30 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 447 | 0 |  |  |  |  | n | 0
2018-10-30 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 530.7 | 0 |  |  |  |  | n | 0
2018-10-30 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 378.6 | 0 |  |  |  |  | n | 0
2018-10-30 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 600 | 0 |  |  |  |  | n | 0
2018-10-30 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-30 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 698.9 | 0 |  |  |  |  | n | 0
2018-10-31 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 84 | 0 |  |  |  |  | n | 0
2018-10-31 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 399.5 | 0 |  |  |  |  | n | 0
2018-10-31 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 569.9 | 0 |  |  |  |  | n | 0
2018-10-31 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 633.1 | 0 |  |  |  |  | n | 0
2018-10-31 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-10-31 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 654.4 | 0 |  |  |  |  | n | 0
2018-11-01 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 637.5 | 0 |  |  |  |  | n | 0
2018-11-01 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 270.7 | 0 |  |  |  |  | n | 0
2018-11-01 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 253.9 | 0 |  |  |  |  | n | 0
2018-11-01 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/55ee5aaa-b5e1-4fae-a28f-73011ecceab6/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-01 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/55ee5aaa-b5e1-4fae-a28f-73011ecceab6/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-01 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/55ee5aaa-b5e1-4fae-a28f-73011ecceab6/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-01 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/55ee5aaa-b5e1-4fae-a28f-73011ecceab6/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-01 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/55ee5aaa-b5e1-4fae-a28f-73011ecceab6/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-01 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/55ee5aaa-b5e1-4fae-a28f-73011ecceab6/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-01 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/55ee5aaa-b5e1-4fae-a28f-73011ecceab6/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-01 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 500.3 | 0 |  |  |  |  | n | 0
2018-11-01 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-01 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 634.4 | 0 |  |  |  |  | n | 0
2018-11-02 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 694.3 | 0 |  |  |  |  | n | 0
2018-11-02 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/a4e8cff4-de8b-4a07-8105-8c1b79474d64/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-02 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/a4e8cff4-de8b-4a07-8105-8c1b79474d64/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-02 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/a4e8cff4-de8b-4a07-8105-8c1b79474d64/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-02 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/a4e8cff4-de8b-4a07-8105-8c1b79474d64/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-02 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/a4e8cff4-de8b-4a07-8105-8c1b79474d64/1 | 309 | 723 | 1032 |  |  | 0 |  | 401 | 401 | 401 |  | 309 | 0 |  |  |  |  | n | 0 | Remaining work on newly installed equipment.
2018-11-02 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-02 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-11-03 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-11-03 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 425.4 | 0 |  |  |  |  | n | 0
2018-11-03 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-03 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 347.4 | 0 |  |  |  |  | n | 0
2018-11-04 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-04 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-05 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-05 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-05 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 708 | 0 |  |  |  |  | n | 0
2018-11-05 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 130.8 | 0 |  |  |  |  | n | 0
2018-11-05 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 279.9 | 0 |  |  |  |  | n | 0
2018-11-05 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 303.4 | 0 |  |  |  |  | n | 0
2018-11-05 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-05 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 495.8 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 312.8 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-06 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 494.1 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 96.9 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-07 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 359.6 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 168.3 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 27.4 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 402.8 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-08 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-09 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 272.3 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 193.9 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 56.2 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-10 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 456.4 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 486 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 272.3 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/41a1906d-48c5-4532-8f16-1c4625bb56b9/3 | 516 | 723 | 1239 |  |  | 0 |  | 200 | 0 | 0 |  | 516 | 0 |  |  |  |  | n | 0 | Disconnection of the 420 kV station Kvilldal as part of the construction of the NSL cable.
2018-11-11 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-11 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-11 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-11 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-11 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-11 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-11 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-11 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-12 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-13 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 614.7 | 0 |  |  |  |  | n | 0
2018-11-14 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 368.7 | 0 |  |  |  |  | n | 0
2018-11-14 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-14 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-15 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-16 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-17 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 353.7 | 0 |  |  |  |  | n | 0
2018-11-18 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 487.4 | 0 |  |  |  |  | n | 0
2018-11-18 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 596.5 | 0 |  |  |  |  | n | 0
2018-11-18 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-18 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 353.5 | 0 |  |  |  |  | n | 0
2018-11-19 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 391.7 | 0 |  |  |  |  | n | 0
2018-11-19 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 481.3 | 0 |  |  |  |  | n | 0
2018-11-19 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 343.8 | 0 |  |  |  |  | n | 0
2018-11-19 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 284.7 | 0 |  |  |  |  | n | 0
2018-11-19 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 380 | 0 |  |  |  |  | n | 0
2018-11-19 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 514.9 | 0 |  |  |  |  | n | 0
2018-11-19 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 529.2 | 0 |  |  |  |  | n | 0
2018-11-19 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 704.7 | 0 |  |  |  |  | n | 0
2018-11-19 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 700.9 | 0 |  |  |  |  | n | 0
2018-11-19 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-19 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 449.2 | 0 |  |  |  |  | n | 0
2018-11-20 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 5.8 | 0 |  |  |  |  | n | 0
2018-11-20 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-20 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 141.8 |  |  |  |  | n | 0
2018-11-20 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 164.2 |  |  |  |  | n | 0
2018-11-20 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 196.7 |  |  |  |  | n | 0
2018-11-20 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 157.5 | 0 |  |  |  |  | n | 0
2018-11-20 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 278.2 | 0 |  |  |  |  | n | 0
2018-11-20 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 637.9 | 0 |  |  |  |  | n | 0
2018-11-20 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-20 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 610.6 | 0 |  |  |  |  | n | 0
2018-11-20 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 164.2 | 0 |  |  |  |  | n | 0
2018-11-21 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-21 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 372.1 | 0 |  |  |  |  | n | 0
2018-11-21 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 363.6 | 0 |  |  |  |  | n | 0
2018-11-21 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 460.3 | 0 |  |  |  |  | n | 0
2018-11-21 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 674.3 | 0 |  |  |  |  | n | 0
2018-11-21 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 515.9 | 0 |  |  |  |  | n | 0
2018-11-21 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-21 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 444.1 | 0 |  |  |  |  | n | 0
2018-11-21 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 196.2 | 0 |  |  |  |  | n | 0
2018-11-22 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 551 | 0 |  |  |  |  | n | 0
2018-11-22 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 462.9 | 0 |  |  |  |  | n | 0
2018-11-22 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 371.9 | 0 |  |  |  |  | n | 0
2018-11-22 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 516.8 | 0 |  |  |  |  | n | 0
2018-11-22 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-22 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 583.1 | 0 |  |  |  |  | n | 0
2018-11-23 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 617.1 | 0 |  |  |  |  | n | 0
2018-11-23 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 40.9 | 0 |  |  |  |  | n | 0
2018-11-23 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 5.5 | 0 |  |  |  |  | n | 0
2018-11-23 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 451.5 | 0 |  |  |  |  | n | 0
2018-11-23 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 391.4 | 0 |  |  |  |  | n | 0
2018-11-23 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-23 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-24 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 617.3 | 0 |  |  |  |  | n | 0
2018-11-25 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-25 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-25 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-11-25 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 274.6 | 0 |  |  |  |  | n | 0
2018-11-25 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-11-25 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-25 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-11-26 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 481.7 | 0 |  |  |  |  | n | 0
2018-11-26 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 511.1 | 0 |  |  |  |  | n | 0
2018-11-26 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 431.5 | 0 |  |  |  |  | n | 0
2018-11-26 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-26 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-26 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 200.3 | 0 |  |  |  |  | n | 0
2018-11-26 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 672.6 | 0 |  |  |  |  | n | 0
2018-11-26 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 693.6 | 0 |  |  |  |  | n | 0
2018-11-26 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 344.9 | 0 |  |  |  |  | n | 0
2018-11-26 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 521.8 | 0 |  |  |  |  | n | 0
2018-11-26 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 493.9 | 0 |  |  |  |  | n | 0
2018-11-26 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-26 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-11-27 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 1.9 | 0 |  |  |  |  | n | 0
2018-11-27 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-27 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 428.3 | 0 |  |  |  |  | n | 0
2018-11-27 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 650.4 | 0 |  |  |  |  | n | 0
2018-11-27 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 628 | 0 |  |  |  |  | n | 0
2018-11-27 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 634.9 | 0 |  |  |  |  | n | 0
2018-11-27 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 573.8 | 0 |  |  |  |  | n | 0
2018-11-27 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 715.2 | 0 |  |  |  |  | n | 0
2018-11-27 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-27 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 720 | 0 |  |  |  |  | n | 0
2018-11-27 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 572.2 | 0 |  |  |  |  | n | 0
2018-11-27 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-28 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-28 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 542.6 | 0 |  |  |  |  | n | 0
2018-11-28 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 360.9 | 0 |  |  |  |  | n | 0
2018-11-28 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 302.5 | 0 |  |  |  |  | n | 0
2018-11-28 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-28 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-28 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-11-28 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-28 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 665.1 | 0 |  |  |  |  | n | 0
2018-11-28 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-28 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-28 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 593.5 | 0 |  |  |  |  | n | 0
2018-11-28 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 544.4 | 0 |  |  |  |  | n | 0
2018-11-28 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 493 | 0 |  |  |  |  | n | 0
2018-11-28 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 662.3 | 0 |  |  |  |  | n | 0
2018-11-28 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-28 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-28 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-28 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 566 | 0 |  |  |  |  | n | 0
2018-11-28 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 582.5 | 0 |  |  |  |  | n | 0
2018-11-28 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 419.3 | 0 |  |  |  |  | n | 0
2018-11-28 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 564.2 | 0 |  |  |  |  | n | 0
2018-11-28 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-28 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 566.4 | 0 |  |  |  |  | n | 0
2018-11-29 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 218.6 | 0 |  |  |  |  | n | 0
2018-11-29 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-29 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 593.3 | 0 |  |  |  |  | n | 0
2018-11-29 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 593.4 | 0 |  |  |  |  | n | 0
2018-11-29 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 439.6 | 0 |  |  |  |  | n | 0
2018-11-29 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 538 | 0 |  |  |  |  | n | 0
2018-11-29 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-29 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 686.3 | 0 |  |  |  |  | n | 0
2018-11-30 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 663.3 | 0 |  |  |  |  | n | 0
2018-11-30 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 262.3 | 0 |  |  |  |  | n | 0
2018-11-30 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 437.7 | 0 |  |  |  |  | n | 0
2018-11-30 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 181.3 |  |  |  |  | n | 0
2018-11-30 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-11-30 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-11-30 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-11-30 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 594.9 | 0 |  |  |  |  | n | 0
2018-12-01 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 627.7 | 0 |  |  |  |  | n | 0
2018-12-01 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 541.3 | 0 |  |  |  |  | n | 0
2018-12-01 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-01 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 287.8 | 0 |  |  |  |  | n | 0
2018-12-01 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-02 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-02 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-02 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 246.1 | 0 |  |  |  |  | n | 0
2018-12-02 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 388.4 | 0 |  |  |  |  | n | 0
2018-12-02 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-02 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 96.2 |  |  |  |  | n | 0
2018-12-02 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 144.1 | 0 |  |  |  |  | n | 0
2018-12-02 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 461.5 | 0 |  |  |  |  | n | 0
2018-12-02 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-02 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-03 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 132.4 | 0 |  |  |  |  | n | 0
2018-12-03 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 486.6 |  |  |  |  | n | 0
2018-12-03 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 553 |  |  |  |  | n | 0
2018-12-03 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 700.9 |  |  |  |  | n | 0
2018-12-03 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-03 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-12-03 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-03 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-03 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 533.3 | 0 |  |  |  |  | n | 0
2018-12-04 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 654.5 | 0 |  |  |  |  | n | 0
2018-12-04 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-04 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-05 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-05 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-05 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-05 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-05 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-05 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 472.3 | 0 |  |  |  |  | n | 0
2018-12-05 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 534.9 | 0 |  |  |  |  | n | 0
2018-12-05 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 652.3 | 0 |  |  |  |  | n | 0
2018-12-05 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 33.3 | 0 |  |  |  |  | n | 0
2018-12-06 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 421.5 | 0 |  |  |  |  | n | 0
2018-12-06 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 325.7 | 0 |  |  |  |  | n | 0
2018-12-06 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 153.8 | 0 |  |  |  |  | n | 0
2018-12-06 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 465.2 |  |  |  |  | n | 0
2018-12-06 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 619 |  |  |  |  | n | 0
2018-12-06 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-06 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-12-06 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 306.2 | 0 |  |  |  |  | n | 0
2018-12-06 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 632 | 0 |  |  |  |  | n | 0
2018-12-06 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-06 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-07 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 433.7 | 0 |  |  |  |  | n | 0
2018-12-07 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 163.9 |  |  |  |  | n | 0
2018-12-07 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 446.5 |  |  |  |  | n | 0
2018-12-07 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 378.3 |  |  |  |  | n | 0
2018-12-07 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-07 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 668.6 |  |  |  |  | n | 0
2018-12-07 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 49.6 |  |  |  |  | n | 0
2018-12-07 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 569.4 | 0 |  |  |  |  | n | 0
2018-12-07 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-07 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-07 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-07 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-07 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 461.2 | 0 |  |  |  |  | n | 0
2018-12-07 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 86.3 | 0 |  |  |  |  | n | 0
2018-12-07 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 52.8 | 0 |  |  |  |  | n | 0
2018-12-07 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-07 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-07 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-07 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 701.1 | 0 |  |  |  |  | n | 0
2018-12-07 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 183.6 | 0 |  |  |  |  | n | 0
2018-12-07 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-07 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 380.3 | 0 |  |  |  |  | n | 0
2018-12-07 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 448.8 | 0 |  |  |  |  | n | 0
2018-12-07 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 652.2 | 0 |  |  |  |  | n | 0
2018-12-08 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 251.5 | 0 |  |  |  |  | n | 0
2018-12-08 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 477.4 | 0 |  |  |  |  | n | 0
2018-12-08 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 141.6 |  |  |  |  | n | 0
2018-12-08 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-08 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-08 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-08 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 202.4 |  |  |  |  | n | 0
2018-12-08 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 224.4 |  |  |  |  | n | 0
2018-12-08 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 394.6 | 0 |  |  |  |  | n | 0
2018-12-08 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 399.2 | 0 |  |  |  |  | n | 0
2018-12-08 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-08 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-12-09 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-09 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 619 |  |  |  |  | n | 0
2018-12-09 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-09 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-09 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-09 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 563.5 |  |  |  |  | n | 0
2018-12-09 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 10.2 | 0 |  |  |  |  | n | 0
2018-12-09 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-09 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 493.3 | 0 |  |  |  |  | n | 0
2018-12-09 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 302.1 | 0 |  |  |  |  | n | 0
2018-12-09 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-09 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 549.9 | 0 |  |  |  |  | n | 0
2018-12-10 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 463.3 | 0 |  |  |  |  | n | 0
2018-12-10 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 464.4 | 0 |  |  |  |  | n | 0
2018-12-10 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 96.2 | 0 |  |  |  |  | n | 0
2018-12-10 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 34.5 | 0 |  |  |  |  | n | 0
2018-12-10 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 42.2 | 0 |  |  |  |  | n | 0
2018-12-10 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-10 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-12-10 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-10 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 565.3 | 0 |  |  |  |  | n | 0
2018-12-11 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 662 | 0 |  |  |  |  | n | 0
2018-12-11 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 276.6 | 0 |  |  |  |  | n | 0
2018-12-11 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 59.1 | 0 |  |  |  |  | n | 0
2018-12-11 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 67.5 | 0 |  |  |  |  | n | 0
2018-12-11 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 154.8 | 0 |  |  |  |  | n | 0
2018-12-11 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 527.4 | 0 |  |  |  |  | n | 0
2018-12-11 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-11 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-12 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-12 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-12 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-12 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-12 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-12 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 702.6 | 0 |  |  |  |  | n | 0
2018-12-12 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-12 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 305.6 | 0 |  |  |  |  | n | 0
2018-12-12 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-13 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-12-13 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 338.8 | 0 |  |  |  |  | n | 0
2018-12-13 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-13 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-13 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-13 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 560.6 | 0 |  |  |  |  | n | 0
2018-12-13 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 668.7 | 0 |  |  |  |  | n | 0
2018-12-13 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-13 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 581.8 | 0 |  |  |  |  | n | 0
2018-12-14 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 712.4 | 0 |  |  |  |  | n | 0
2018-12-14 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-12-14 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-14 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 54 | 0 |  |  |  |  | n | 0
2018-12-14 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 673 | 0 |  |  |  |  | n | 0
2018-12-14 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-14 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-15 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 128.5 | 0 |  |  |  |  | n | 0
2018-12-15 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 506.8 | 0 |  |  |  |  | n | 0
2018-12-15 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 479 | 0 |  |  |  |  | n | 0
2018-12-15 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-15 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-15 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-15 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-12-15 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-15 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 161.7 | 0 |  |  |  |  | n | 0
2018-12-16 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 134 | 0 |  |  |  |  | n | 0
2018-12-16 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-16 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-17 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 540.7 | 0 |  |  |  |  | n | 0
2018-12-17 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-17 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-17 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-17 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-17 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-17 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-17 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 335 | 0 |  |  |  |  | n | 0
2018-12-17 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 243.1 | 0 |  |  |  |  | n | 0
2018-12-17 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-17 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-17 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-17 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 211 | 0 |  |  |  |  | n | 0
2018-12-17 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 81.9 | 0 |  |  |  |  | n | 0
2018-12-17 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-17 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-17 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-17 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-17 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 519.9 | 0 |  |  |  |  | n | 0
2018-12-17 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-17 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-17 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-17 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-17 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 127.8 | 0 |  |  |  |  | n | 0
2018-12-18 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 619 | 0 |  |  |  |  | n | 0
2018-12-18 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 21.5 | 0 |  |  |  |  | n | 0
2018-12-18 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 100.5 | 0 |  |  |  |  | n | 0
2018-12-18 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-18 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 536.7 | 0 |  |  |  |  | n | 0
2018-12-18 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 393.8 | 0 |  |  |  |  | n | 0
2018-12-18 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 88.5 | 0 |  |  |  |  | n | 0
2018-12-19 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 707.5 | 0 |  |  |  |  | n | 0
2018-12-19 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 553.7 | 0 |  |  |  |  | n | 0
2018-12-19 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 642 | 0 |  |  |  |  | n | 0
2018-12-19 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-19 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-20 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-20 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-20 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-20 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-20 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 386.8 |  |  |  |  | n | 0
2018-12-20 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-20 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-20 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-20 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 527.8 | 0 |  |  |  |  | n | 0
2018-12-20 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-21 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 320.5 |  |  |  |  | n | 0
2018-12-21 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 533.1 |  |  |  |  | n | 0
2018-12-21 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 629.2 |  |  |  |  | n | 0
2018-12-21 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-21 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-21 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-12-21 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-21 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-21 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-21 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-21 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-21 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-21 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-21 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-21 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-21 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-21 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 241.7 | 0 |  |  |  |  | n | 0
2018-12-21 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-21 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-21 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-21 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 484.4 | 0 |  |  |  |  | n | 0
2018-12-21 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 379 | 0 |  |  |  |  | n | 0
2018-12-21 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 109.4 | 0 |  |  |  |  | n | 0
2018-12-21 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 295.8 | 0 |  |  |  |  | n | 0
2018-12-22 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 641.6 | 0 |  |  |  |  | n | 0
2018-12-22 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 22.6 | 0 |  |  |  |  | n | 0
2018-12-22 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 286.5 |  |  |  |  | n | 0
2018-12-22 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-22 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-22 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-22 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-22 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-22 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 104 |  |  |  |  | n | 0
2018-12-22 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 515 | 0 |  |  |  |  | n | 0
2018-12-22 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-22 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-22 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-22 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-22 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 199.9 | 0 |  |  |  |  | n | 0
2018-12-22 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-22 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 378.1 | 0 |  |  |  |  | n | 0
2018-12-22 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-22 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-22 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-22 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-22 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-22 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-22 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-23 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-23 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-23 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 157.3 | 0 |  |  |  |  | n | 0
2018-12-23 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 461.7 |  |  |  |  | n | 0
2018-12-23 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-23 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 292.3 |  |  |  |  | n | 0
2018-12-23 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 326.7 | 0 |  |  |  |  | n | 0
2018-12-23 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 496 | 0 |  |  |  |  | n | 0
2018-12-23 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 26.7 |  |  |  |  | n | 0
2018-12-23 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 590.5 | 0 |  |  |  |  | n | 0
2018-12-23 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-23 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-23 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-23 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 497.1 | 0 |  |  |  |  | n | 0
2018-12-23 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 277.2 | 0 |  |  |  |  | n | 0
2018-12-23 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-23 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-23 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-23 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-23 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-23 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-23 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-23 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 288.2 | 0 |  |  |  |  | n | 0
2018-12-23 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 338.3 | 0 |  |  |  |  | n | 0
2018-12-24 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 280.7 |  |  |  |  | n | 0
2018-12-24 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-24 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-24 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-24 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-24 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-24 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 689.5 |  |  |  |  | n | 0
2018-12-24 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 70.5 |  |  |  |  | n | 0
2018-12-24 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 548.5 | 0 |  |  |  |  | n | 0
2018-12-24 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 476.2 | 0 |  |  |  |  | n | 0
2018-12-24 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-24 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 140.9 | 0 |  |  |  |  | n | 0
2018-12-25 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 47.5 |  |  |  |  | n | 0
2018-12-25 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-25 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-25 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 335.7 | 0 |  |  |  |  | n | 0
2018-12-25 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 627.5 | 0 |  |  |  |  | n | 0
2018-12-25 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 8.5 | 0 |  |  |  |  | n | 0
2018-12-25 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 592.5 | 0 |  |  |  |  | n | 0
2018-12-25 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 26.5 |  |  |  |  | n | 0
2018-12-25 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 515 |  |  |  |  | n | 0
2018-12-25 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-25 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-25 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 567 | 0 |  |  |  |  | n | 0
2018-12-25 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 647.2 | 0 |  |  |  |  | n | 0
2018-12-26 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 28.2 | 0 |  |  |  |  | n | 0
2018-12-26 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 13.3 | 0 |  |  |  |  | n | 0
2018-12-26 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 87.7 |  |  |  |  | n | 0
2018-12-26 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-26 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 111.4 | 0 |  |  |  |  | n | 0
2018-12-26 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 35.4 |  |  |  |  | n | 0
2018-12-26 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 583.6 | 0 |  |  |  |  | n | 0
2018-12-26 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 696.9 | 0 |  |  |  |  | n | 0
2018-12-26 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 385.3 | 0 |  |  |  |  | n | 0
2018-12-26 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 496.2 | 0 |  |  |  |  | n | 0
2018-12-26 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-26 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 657.9 | 0 |  |  |  |  | n | 0
2018-12-27 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 308.2 | 0 |  |  |  |  | n | 0
2018-12-27 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 64.5 |  |  |  |  | n | 0
2018-12-27 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 611.5 |  |  |  |  | n | 0
2018-12-27 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 619 |  |  |  |  | n | 0
2018-12-27 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-27 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-27 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-27 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 683.5 | 0 |  |  |  |  | n | 0
2018-12-28 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 64.5 | 0 |  |  |  |  | n | 0
2018-12-28 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-28 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-28 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-28 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-28 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-28 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-28 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 676.8 | 0 |  |  |  |  | n | 0
2018-12-28 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 57.8 | 0 |  |  |  |  | n | 0
2018-12-29 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 676.8 | 0 |  |  |  |  | n | 0
2018-12-29 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 542.3 | 0 |  |  |  |  | n | 0
2018-12-29 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-29 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 186.3 |  |  |  |  | n | 0
2018-12-29 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 244.1 |  |  |  |  | n | 0
2018-12-29 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 700.2 |  |  |  |  | n | 0
2018-12-29 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 152.8 |  |  |  |  | n | 0
2018-12-29 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-29 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-29 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-29 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-29 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-29 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-29 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-29 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 128 | 0 |  |  |  |  | n | 0
2018-12-29 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 64.2 | 0 |  |  |  |  | n | 0
2018-12-29 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-29 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-29 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-29 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-29 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-29 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-29 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-29 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 398.1 | 0 |  |  |  |  | n | 0
2018-12-30 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 508.3 | 0 |  |  |  |  | n | 0
2018-12-30 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 220.6 | 0 |  |  |  |  | n | 0
2018-12-30 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 436.7 | 0 |  |  |  |  | n | 0
2018-12-30 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 714.8 | 0 |  |  |  |  | n | 0
2018-12-30 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 148.3 | 0 |  |  |  |  | n | 0
2018-12-30 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 470.7 |  |  |  |  | n | 0
2018-12-30 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 187.4 |  |  |  |  | n | 0
2018-12-30 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 431.6 | 0 |  |  |  |  | n | 0
2018-12-30 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-30 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-30 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 00 - 01 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-31 | 01 - 02 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | n | 0
2018-12-31 | 02 - 03 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 104 |  |  |  |  | n | 0
2018-12-31 | 03 - 04 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 723 |  |  |  |  | n | 0
2018-12-31 | 04 - 05 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 630.9 |  |  |  |  | n | 0
2018-12-31 | 05 - 06 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 11.9 |  |  |  |  | n | 0
2018-12-31 | 06 - 07 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 35.9 | 0 |  |  |  |  | n | 0
2018-12-31 | 07 - 08 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 654.9 | 0 |  |  |  |  | n | 0
2018-12-31 | 08 - 09 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 09 - 10 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 10 - 11 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 11 - 12 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 12 - 13 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 13 - 14 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 14 - 15 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 15 - 16 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 16 - 17 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 17 - 18 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 18 - 19 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 19 - 20 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 723 | 0 |  |  |  |  | n | 0
2018-12-31 | 20 - 21 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 104 | 0 |  |  |  |  | n | 0
2018-12-31 | 21 - 22 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 58.9 |  |  |  |  | n | 0
2018-12-31 | 22 - 23 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 41 | 0 |  |  |  |  | n | 0
2018-12-31 | 23 - 00 | n | n |  | 723 | 723 | 1446 |  |  | 0 |  | 0 | 0 | 0 |  | 0 | 533.4 |  |  |  |  | n | 0

## Tabel 4 Bronnen
Tabel 4 - Gebruikte bronnen
| day ahead capacity: | https://www.nordpoolgroup.com/globalassets/marketdata-excel-files/market-coupling-capacities_2018_hourly.xls
| intraday initial capacity (until June 12, 2018): | https://www.nordpoolgroup.com/globalassets/marketdata-excel-files/elbas-initial-capacity_2018_hourly.xls | *1)
| day ahead flow: | https://www.nordpoolgroup.com/globalassets/marketdata-excel-files/market-coupling-flow_2018_hourly.xls
| intraday flow (until June 12, 2018): | https://www.nordpoolgroup.com/globalassets/marketdata-excel-files/elbas-flow_2018_hourly.xls | *1)
| UMM's: | https://umm.nordpoolgroup.com/#/messages?publicationDate=custom&publicationDateStart=2017-12-01&publicationDateStop=2018-12-01&eventDate=custom&eventDateStart=2017-12-01&eventDateStop=2018-12-31&connections=NL-NO2&connections=NO2-NL
*1) - as from the go-live of the European Cross-Border Intraday (XBID) Solution on June 12, 2018 the (ELBAS) data for intraday is no longer available via the abovementioned website of Nordpoolgroup.
The absence of this data has no impact on the proposal of TenneT as the maximum malus is already proposed for the year 2018.