## Tabel 1 Adresgegevens
Tabel 1 - Adresgegevens
Informatieverzoek van ACM/Directie Energie in het kader van CODATA
Onderwerp | NorNed bonus/malus
Referentiejaar | 2019
DOX-nummer | ACM/19/039627
Datum ingevuld | 2020-01-31
Adresgegevens
Naam bedrijf | TenneT TSO B.V.
Adres | Postbus 718
Postcode | 6800 AS
Plaats | Arnhem
Contactgegevens ACM ten behoeve van deze uitvraag
Postbus 16326
2500 BH DEN HAAG
tel : 070 - 722 2194
e-mail : CODATA_Netbeheerders@acm.nl

## Tabel 2 Berekening bonus-malus
Tabel 2 - Berekening bonus/malus
Beschrijving resultaat
Op dit tabblad berekent de ACM de bonus/malus (het prikkelbedrag) voor de relatieve beschikbaarheid van de NorNed-kabel in 2019. TenneT mag dit bedrag in het boekjaar 2020 met de veilinggelden verrekenen.
Omschrijving | Eenheid | Constante | Bron | Hyperlink | Opmerking
Ophalen gegevens voor berekening
CPI
CPI 2005 | % | 1.1% | CBS Statline |  | De relatieve wijziging van de consumentenprijsindex wordt berekend uit het quotiënt van deze index, gepubliceerd in de vierde maand voorafgaande aan het jaar t, en van deze index, gepubliceerd
CPI 2006 | % | 1.8% | CBS Statline |  | in de zestiende maand voorafgaande aan het jaar t, zoals deze maandelijks wordt vastgesteld door het CBS.
CPI 2007 | % | 1.4% | CBS Statline |  | De gegevens zijn afkomstig uit StatLine, zie voor recente CPI-cijfers: https://opendata.cbs.nl/statline/#/CBS/nl/dataset/70936ned/table?ts=1532343719053.
CPI 2008 | % | 1.1% | CBS Statline
CPI 2009 | % | 3.2% | CBS Statline
CPI 2010 | % | 0.3% | CBS Statline
CPI 2011 | % | 1.5% | CBS Statline
CPI 2012 | % | 2.6% | CBS Statline
CPI 2013 | % | 2.3% | CBS Statline
CPI 2014 | % | 2.8% | CBS Statline
CPI 2015 | % | 1% | CBS Statline
CPI 2016 | % | 0.8% | CBS Statline
CPI 2017 | % | 0.2% | CBS Statline
CPI 2018 | % | 1.4% | CBS Statline
CPI 2019 | % | 2.1% | CBS Statline
Bonus/malus
Bonus/malus per 1% beschikbaarheid boven norm | EUR | 400000 | NorNed-besluit, bijlage A, rn. 16 | hier
Maximum bonus/malus | EUR | 1200000 | NorNed-besluit, bijlage A, rn. 16 | hier
Capaciteit
Capaciteit NorNed exclusief netverliezen | MW | 700
Capaciteit NorNed inclusief netverliezen | MW | 723
Multiplier netverliezen |  | 1.0329 |  |  | Dit getal wordt gebruikt om in kolom M van Tabel 3 de beschikbare capaciteit inclusief netverliezen om te zetten naar de beschikbare capaciteit exclusief netverliezen.
Nominale capaciteit | MW | 683.86 | Vaststelling nominale capaciteit NorNed-kabel, rn. 34 | hier
Norm relatieve beschikbaarheid | % | 95.62% | NorNed-besluit, bijlage A, rn. 16 | hier
Restricties
Totaal DA-restricties | MW | 1315232
Beperkingen force majeure | MW | 0
Beperkingen Noorse AC net | MW | 69110
Restrictie TenneT excl. intraday | MW | 1246122
Restrictie TenneT incl. intraday | MW | 1246122
Correcties | MW | 0
Uren
Totaal aantal uren in 2019 | uren | 8760
Berekening bonus/malus
Beperkingen door TenneT | MW | 1246122
Beschikbaar gestelde capaciteit in 2019 | MW | 4885878
Nominale capaciteit in 2019 | MW | 5990613.6
Relatieve beschikbaarheid | % | 81.56%
Verschil tussen relatieve beschikbaarheid en norm | %-punt | -14.0611
Bonus/malus | EUR | -5624443.7085
Inflatie van 2004 naar 2019 | 1+% | 1.2632
Bonus/malus inclusief inflatiecorrectie | EUR | -1515812.194

## Tabel 3 Beschikbaarheid NorNed
Tabel 3 - Beschikbaarheid NorNed |  |  |  |  | day ahead |  |  | intraday |  |  | restrictie |  |  | day ahead flow |  | intraday flow
Dag | uren | force majeure: j/n | Noorse AC net restrictie: j/n | hyperlink naar UMM | NO2 > NL | NL > NO2 | totaal | NO2 > NL | NL > NO2 | totaal | totaal DA op NorNed | TenneT incl. intraday | TenneT excl. intraday | NO2 > NL | NL > NO2 | NO2 > NL | NL > NO2 | corr TenneT j/n | corr. Beschibaarheid (MW) | Toelichting TenneT
2019-01-01 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 85.6 | 0
2019-01-01 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 704.6 | 0
2019-01-01 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-01 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 340.7 | 0
2019-01-01 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-01 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-01 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 112.6 | 0
2019-01-01 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 627.1 | 0
2019-01-01 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 8.1 | 0
2019-01-01 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 290.8 | 0
2019-01-01 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-01 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-01 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-01 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 559.7 | 0
2019-01-01 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 183.1 | 0
2019-01-01 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 170.6 | 0
2019-01-01 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 466.9 | 0
2019-01-01 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-01 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 155.8 | 0
2019-01-01 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 89.6
2019-01-01 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-01 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 285.9
2019-01-01 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 63 | 0
2019-01-01 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 113.3
2019-01-02 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-02 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 342.9
2019-01-02 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 304.5
2019-01-02 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 581.8
2019-01-02 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 479.7
2019-01-02 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 521.9
2019-01-02 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 333.3
2019-01-02 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-02 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 169.7 | 0
2019-01-02 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 364 | 0
2019-01-02 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 423.4 | 0
2019-01-02 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 231.8 | 0
2019-01-02 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 109.8 | 0
2019-01-02 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 395 | 0
2019-01-02 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 719.5 | 0
2019-01-02 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-02 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-02 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-02 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-02 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-02 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-02 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-02 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 610.2 | 0
2019-01-02 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 168.6 | 0
2019-01-03 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-03 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-01-03 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-03 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-03 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-03 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-01-03 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-03 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-03 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-03 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 462.9 | 0
2019-01-03 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-04 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 2.5 | 0
2019-01-04 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 128.4
2019-01-04 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-04 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-04 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-04 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-04 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-04 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 699 | 0
2019-01-04 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 525.4 | 0
2019-01-04 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 290.7 | 0
2019-01-04 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 306.3 | 0
2019-01-05 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 171 | 0
2019-01-05 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 316.2
2019-01-05 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 213.7
2019-01-05 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 484.7
2019-01-05 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-05 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-05 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-05 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 280.7
2019-01-05 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 42.9 | 0
2019-01-05 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 643.9 | 0
2019-01-05 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 599.6 | 0
2019-01-05 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 662.5 | 0
2019-01-05 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-05 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-05 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-05 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-05 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-05 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-05 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-05 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-05 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-05 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 620.2 | 0
2019-01-05 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 417.4 | 0
2019-01-05 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-06 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 253.9 | 0
2019-01-06 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-06 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-06 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-06 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-01-06 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-06 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-06 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-06 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-06 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-01-06 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-06 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-06 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-06 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 689.3 | 0
2019-01-06 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 70.3 | 0
2019-01-06 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-06 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-06 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-06 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-06 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-06 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-06 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-06 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-06 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 483.2 | 0
2019-01-07 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 135.8
2019-01-07 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-07 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-07 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 572
2019-01-07 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 691.4
2019-01-07 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 72.4
2019-01-07 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 546.6 | 0
2019-01-07 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-07 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-07 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-07 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-07 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-07 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-07 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-07 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-07 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-07 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-07 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-07 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 437.6 | 0
2019-01-07 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-07 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-07 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-07 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 316.1
2019-01-07 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-08 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-08 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 720.2
2019-01-08 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-08 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-08 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-08 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-01-08 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-08 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 456.8 | 0
2019-01-08 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-08 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-08 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-08 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 545.3 | 0
2019-01-08 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 73.7
2019-01-08 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 305.7
2019-01-08 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 28.6 | 0
2019-01-08 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 178.2 | 0
2019-01-08 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 701.2 | 0
2019-01-08 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-08 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 486.6 | 0
2019-01-08 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 19.4
2019-01-08 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-08 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 129.6 | 0
2019-01-08 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 144.6 | 0
2019-01-08 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 94.3
2019-01-09 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 713.3
2019-01-09 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-09 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-09 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-09 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-09 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 586.1
2019-01-09 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 32.9 | 0
2019-01-09 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 651.9 | 0
2019-01-09 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-09 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-09 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-09 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 621.2 | 0
2019-01-09 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 2.2 | 0
2019-01-09 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-09 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 454.7 | 0
2019-01-09 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-09 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-09 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-09 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-09 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 454.1 | 0
2019-01-09 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 142.1 | 0
2019-01-09 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 60.1
2019-01-09 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 338.8 | 0
2019-01-09 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-10 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-10 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-10 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-10 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-10 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-10 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-10 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-01-10 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-10 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-10 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 129.8 | 0
2019-01-10 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 453 | 0
2019-01-10 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 700.5 | 0
2019-01-10 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-10 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-10 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-10 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-10 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-10 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-10 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-10 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-10 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-10 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-10 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-10 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 119 | 0
2019-01-11 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 500
2019-01-11 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-11 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 540.6
2019-01-11 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-11 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 480.2
2019-01-11 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-11 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-01-11 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 120.8 | 0
2019-01-11 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-11 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-11 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-11 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-11 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 716.1 | 0
2019-01-11 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 678.5 | 0
2019-01-11 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 452.6 | 0
2019-01-11 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 85.7 | 0
2019-01-11 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 117.6 | 0
2019-01-11 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-11 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 197.1 | 0
2019-01-11 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 176.6 | 0
2019-01-11 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 167.8 | 0
2019-01-11 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 94
2019-01-11 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 297.9
2019-01-11 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 607.8
2019-01-12 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 64.6
2019-01-12 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 185
2019-01-12 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 49.7
2019-01-12 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 668.7
2019-01-12 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 262.4
2019-01-12 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-12 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/f4d469d2-9778-45f8-a65c-39eb76e4da66/1 | 619 | 723 | 1342 |  |  | 0 | 100 | 100 | 100 | 0 | 619 |  |  |  |  | Foreseen maintenance, maintenance in the NorNed Eemshaven region TenneT
2019-01-12 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/f4d469d2-9778-45f8-a65c-39eb76e4da66/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Foreseen maintenance, maintenance in the NorNed Eemshaven region TenneT
2019-01-12 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/f4d469d2-9778-45f8-a65c-39eb76e4da66/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Foreseen maintenance, maintenance in the NorNed Eemshaven region TenneT
2019-01-12 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/f4d469d2-9778-45f8-a65c-39eb76e4da66/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Foreseen maintenance, maintenance in the NorNed Eemshaven region TenneT
2019-01-12 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/f4d469d2-9778-45f8-a65c-39eb76e4da66/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Foreseen maintenance, maintenance in the NorNed Eemshaven region TenneT
2019-01-12 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/f4d469d2-9778-45f8-a65c-39eb76e4da66/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Foreseen maintenance, maintenance in the NorNed Eemshaven region TenneT
2019-01-12 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/f4d469d2-9778-45f8-a65c-39eb76e4da66/1 | 619 | 723 | 1342 |  |  | 0 | 100 | 100 | 100 | 271.1 | 0 |  |  |  |  | Foreseen maintenance, maintenance in the NorNed Eemshaven region TenneT
2019-01-12 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-12 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 168.8 | 0
2019-01-12 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 257.5 | 0
2019-01-12 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 1 | 0
2019-01-12 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 620 | 0
2019-01-12 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 1 | 0
2019-01-12 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 494.6
2019-01-12 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 502.4
2019-01-12 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-12 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 415
2019-01-12 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 328.8
2019-01-13 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 290.2 | 0
2019-01-13 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 237.1
2019-01-13 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-13 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-13 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-13 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-13 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-13 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-13 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-13 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 310.7
2019-01-13 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-13 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 282.4 | 0
2019-01-13 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 611.6 | 0
2019-01-13 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 185.8 | 0
2019-01-13 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-13 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 88.8 | 0
2019-01-13 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 414.7 | 0
2019-01-13 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-13 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 352.9 | 0
2019-01-13 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 235.1 | 0
2019-01-13 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 51.6
2019-01-13 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 535.7
2019-01-13 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-13 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-14 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 710.1
2019-01-14 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-14 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 640.1
2019-01-14 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 701.3
2019-01-14 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-14 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 205.1
2019-01-14 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 140.8 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 304.5 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 196.5 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 146.9 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 528.3 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 499.5 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 79 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-14 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 315.2 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 378.3 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 723 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 723 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 723 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 723 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 723 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 109.2 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 509.8 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 145.3 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 104.3 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 253.7 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 31.3 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 81.9 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 183.8 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 546.4 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 117.4 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-15 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 297.1 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 723 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 723 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 723 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 723 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 723 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 723 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 169.1 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 449.9 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 308.7 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 365.5 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 8.3 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 242.3 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 305.1 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-16 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 619 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 542.1 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 663.7 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 501.8 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 414.8 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 204.2 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 309.3 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 420.1 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 477.8 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 462.9 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 48.9 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 619 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 173.4 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 717.2 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-17 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 98.2 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 520.8 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 181.2 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 481.3 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 619.2 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0.2 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 312 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/c1387146-50e1-4959-a9e2-50f484627f5d/5 | 532 | 723 | 1255 |  |  | 0 | 185 | 0 | 0 | 532 | 0 |  |  |  |  | Foreseen maintenance. Installation of current transformers in Kvilldal substation.
2019-01-18 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 424.9 | 0
2019-01-18 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-18 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 598.7 | 0
2019-01-18 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-18 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-18 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 424.9 | 0
2019-01-18 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-18 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-19 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-01-19 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 156.7 | 0
2019-01-19 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-19 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 344.6 | 0
2019-01-19 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 183.3 | 0
2019-01-19 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 709.7 | 0
2019-01-19 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 90.7 | 0
2019-01-19 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-19 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-19 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-19 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-20 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-20 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-20 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-01-20 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-20 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-20 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-20 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-01-20 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 423.8
2019-01-20 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 24.2 | 0
2019-01-20 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 643.2 | 0
2019-01-20 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-20 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 694.9 | 0
2019-01-20 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 298.3 | 0
2019-01-20 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-20 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-20 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-20 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-20 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-20 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-20 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-20 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-20 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-20 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-20 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-21 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-21 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-21 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-21 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-21 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-21 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-21 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-01-21 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 419.1 | 0
2019-01-21 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 405.8 | 0
2019-01-21 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 376.6 | 0
2019-01-21 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 379.3 | 0
2019-01-21 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 341.8 | 0
2019-01-21 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 319.5 | 0
2019-01-21 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 416.1 | 0
2019-01-21 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 141.6 | 0
2019-01-21 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 17.1 | 0
2019-01-21 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-21 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-21 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-21 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-21 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-21 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-01-21 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-01-21 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-22 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-22 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-22 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-22 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 498.1
2019-01-22 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 250.8
2019-01-22 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-22 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-01-22 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 229.4
2019-01-22 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 265.7
2019-01-22 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-22 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 107.6 | 0
2019-01-22 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-22 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-22 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-22 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-22 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-22 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-22 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-22 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-22 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-22 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-22 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-22 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-01-22 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-23 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-23 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-23 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-01-23 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-23 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-23 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-23 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-01-23 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 557.5 | 0
2019-01-23 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 285 | 0
2019-01-23 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 176.3 | 0
2019-01-23 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-23 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-23 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-01-24 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-24 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 223.2 | 0
2019-01-24 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 93.4 | 0
2019-01-24 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-24 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-24 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-01-24 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-24 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 293.4 | 0
2019-01-24 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 563.4 | 0
2019-01-24 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 691.1 | 0
2019-01-24 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-24 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 405.6 | 0
2019-01-24 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 394.2 | 0
2019-01-24 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 368.5 | 0
2019-01-24 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 307.7 | 0
2019-01-24 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 674.4 | 0
2019-01-24 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 398.2 | 0
2019-01-24 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 356.2 | 0
2019-01-24 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-24 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-24 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-24 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-24 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-24 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-25 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-25 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-25 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 226.2 | 0
2019-01-25 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-25 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-01-25 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-01-25 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-25 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 457.7 | 0
2019-01-25 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 397 | 0
2019-01-25 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 702.5 | 0
2019-01-25 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 436.1 | 0
2019-01-25 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 535.9 | 0
2019-01-25 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-25 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-25 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-25 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-25 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 635.8 | 0
2019-01-25 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-01-25 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 592.7 | 0
2019-01-25 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 26.3
2019-01-25 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 645.3
2019-01-25 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-25 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-25 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-01-26 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Filter problems in NL
2019-01-26 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Filter problems in NL
2019-01-26 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-26 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-26 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-26 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-26 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-26 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-26 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-26 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-26 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-26 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-26 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-26 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-26 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-26 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-26 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 332 |  |  |  |  | Filter problems in NL
2019-01-26 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-26 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 86.9 | 0 |  |  |  |  | Filter problems in NL
2019-01-26 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-26 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-26 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-26 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-26 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 146 | 0 |  |  |  |  | Filter problems in NL
2019-01-27 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Filter problems in NL
2019-01-27 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 210.3 |  |  |  |  | Filter problems in NL
2019-01-27 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-27 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-27 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 18.9 |  |  |  |  | Filter problems in NL
2019-01-27 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 270.4 |  |  |  |  | Filter problems in NL
2019-01-28 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 8.1 | 0 |  |  |  |  | Filter problems in NL
2019-01-28 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-28 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 293.7 |  |  |  |  | Filter problems in NL
2019-01-28 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-28 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 294.6 |  |  |  |  | Filter problems in NL
2019-01-28 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-28 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-28 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 126.5 |  |  |  |  | Filter problems in NL
2019-01-28 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-28 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-29 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-29 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-29 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-29 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-29 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-29 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-29 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Filter problems in NL
2019-01-29 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 405.9 |  |  |  |  | Filter problems in NL
2019-01-29 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-29 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-29 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/2a6d281c-caa8-4cf9-859f-edd616a80f81/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Filter problems in NL
2019-01-30 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-30 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-01-31 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/f0494428-cfc9-45f2-97eb-c6ef1a77341b/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-01 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-02 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-03 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-04 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-05 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5974f159-c7f6-45f2-a72d-75216810cf80/7 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure in the control system
2019-02-06 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-02-06 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-06 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-06 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-06 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-06 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-06 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 543.6
2019-02-06 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 524.1
2019-02-06 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 9.4
2019-02-06 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-06 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 110.1 | 0
2019-02-06 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 49.8 | 0
2019-02-06 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 257.2 | 0
2019-02-06 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 52.5 | 0
2019-02-06 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-06 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-06 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-06 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-06 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-06 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 427 | 0
2019-02-06 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-06 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-06 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-06 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-02-07 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 487.4
2019-02-07 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 322.5
2019-02-07 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 113.3 | 0
2019-02-07 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 475.1 | 0
2019-02-07 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 136.4 | 0
2019-02-07 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-07 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 222.9
2019-02-07 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-02-07 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 490.8
2019-02-07 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-07 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-08 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 708.7
2019-02-08 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-08 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-08 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-08 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-08 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-08 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 178.6
2019-02-08 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 440.4 | 0
2019-02-08 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-02-08 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-02-08 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-02-08 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-02-08 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-02-08 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 106.2 | 0
2019-02-08 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 358.9
2019-02-08 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-08 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-08 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-02-08 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 233.2 | 0
2019-02-08 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 271.9
2019-02-08 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 154
2019-02-08 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 566.7
2019-02-08 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 544
2019-02-08 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 220.5
2019-02-09 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 352.4
2019-02-09 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-09 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-09 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-09 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-09 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-09 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-09 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-09 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 688.6
2019-02-09 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 69.6
2019-02-09 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-09 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 272.7
2019-02-09 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 282.1
2019-02-09 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-09 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-09 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-09 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 520.1
2019-02-09 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 98.9 | 0
2019-02-09 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 692.3 | 0
2019-02-09 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 115.2 | 0
2019-02-09 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 126 | 0
2019-02-09 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 493
2019-02-09 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 102.4
2019-02-09 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 269.3
2019-02-10 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 179.2
2019-02-10 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-10 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-10 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-10 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-10 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-10 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-02-10 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 232.5
2019-02-10 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 366.1
2019-02-10 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 252.9 | 0
2019-02-10 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 652.9 | 0
2019-02-10 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-02-10 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-02-10 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-02-10 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 419.2
2019-02-10 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-10 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 320
2019-02-10 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 88.7 | 0
2019-02-10 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 656.8 | 0
2019-02-10 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 451.9 | 0
2019-02-10 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 57.8 | 0
2019-02-10 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 407.2
2019-02-10 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-10 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-11 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-11 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-11 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-11 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-11 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-02-11 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 619 | 619 | 1238 |  |  | 0 | 100 | 100 | 100 | 0 | 591.1 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-11 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-12 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/7741e1b1-1a48-4708-b40c-e8ce10a13134/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | NorNed cable will be disconnected due to fault correction.
2019-02-13 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-02-13 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-02-13 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-02-13 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-13 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 380.8
2019-02-13 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 720.2
2019-02-14 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-14 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-15 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-16 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-17 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-18 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-19 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-20 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-21 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-22 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-23 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-24 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-25 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-26 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-27 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c9e63bac-a1cf-4fab-9fe6-3d2d9e95bafa/6 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure at Feda station.
2019-02-28 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-02-28 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-02-28 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-02-28 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-02-28 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-02-28 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-01 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-01 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-01 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-01 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-01 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-01 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-01 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-01 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 143.8 | 0
2019-03-01 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 217.7 | 0
2019-03-01 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-01 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 312.9 | 0
2019-03-01 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 460.1 | 0
2019-03-01 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-02 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-02 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-02 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 143.9
2019-03-02 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-02 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 507.7
2019-03-02 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-02 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 288.2
2019-03-02 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 103.3 | 0
2019-03-02 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 722.3 | 0
2019-03-02 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-02 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-02 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 277.3 | 0
2019-03-02 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-02 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-02 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 571.3
2019-03-02 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 220.3
2019-03-02 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-02 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 89.9 | 0
2019-03-02 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 708.9 | 0
2019-03-02 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 197.7 | 0
2019-03-02 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 421.3
2019-03-02 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-02 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-02 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-03 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 672.3
2019-03-03 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 344.6
2019-03-03 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-03 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-03 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-03 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-03 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 532.2
2019-03-03 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-03 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 180.7
2019-03-03 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 438.3 | 0
2019-03-03 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-03 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-03 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-03 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 505.8 | 0
2019-03-03 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 82.1
2019-03-03 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 701.1
2019-03-03 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-03 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-03 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-03 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-03 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 84.5 | 0
2019-03-03 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 1.7
2019-03-03 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-03 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 121.7 | 0
2019-03-04 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 257.5
2019-03-04 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 2.2
2019-03-04 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 469.4
2019-03-04 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 260.1
2019-03-04 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-04 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-04 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-04 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 443.5
2019-03-04 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 162 | 0
2019-03-04 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-04 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-04 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-04 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 287
2019-03-04 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-04 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 329 | 0
2019-03-04 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-04 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-04 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 711.5 | 0
2019-03-04 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 319.8 | 0
2019-03-04 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 640.6 | 0
2019-03-04 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 182.3 | 0
2019-03-04 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 44.4 | 0
2019-03-04 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 243.2
2019-03-04 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 337.9
2019-03-05 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-05 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-05 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-05 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-05 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-05 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-05 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 318.2
2019-03-05 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 209.7 | 0
2019-03-05 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-05 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-05 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-05 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 273.9 | 0
2019-03-05 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 314
2019-03-05 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 537.5
2019-03-05 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 448.2
2019-03-05 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-05 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-05 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 341.4 | 0
2019-03-05 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-05 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-05 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-05 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-05 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-05 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-06 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-06 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-06 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-06 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-06 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-06 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-06 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-06 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-06 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 109.4 | 0
2019-03-06 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-06 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-06 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-06 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 593.6 | 0
2019-03-06 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 634.4 | 0
2019-03-06 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 342.8 | 0
2019-03-06 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 84.8 | 0
2019-03-06 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 390.9 | 0
2019-03-06 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 495.3 | 0
2019-03-06 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 621.5 | 0
2019-03-06 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-06 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-06 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-06 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 253
2019-03-06 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 102.9
2019-03-07 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 721.9
2019-03-07 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-07 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-07 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-07 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-07 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-07 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 636.4
2019-03-07 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 17.4
2019-03-07 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 601.6 | 0
2019-03-07 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 243.2 | 0
2019-03-07 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 154.6 | 0
2019-03-07 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 428.4
2019-03-07 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-07 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-07 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-07 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-07 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-07 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 255.5
2019-03-07 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-07 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 405.8 | 0
2019-03-07 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-07 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-07 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 705.9
2019-03-07 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-08 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-08 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-08 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-08 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-08 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-08 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-08 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-08 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 484 | 0
2019-03-08 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-08 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-08 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 717.3 | 0
2019-03-08 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 98.3 | 0
2019-03-08 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 456.3
2019-03-08 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-08 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-08 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-08 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 541.5
2019-03-08 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 77.5 | 0
2019-03-08 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 696.5 | 0
2019-03-08 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-08 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-08 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-03-08 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-08 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 598.2
2019-03-09 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 20.8 | 0
2019-03-09 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 526 | 0
2019-03-09 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 93
2019-03-09 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 712
2019-03-09 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-09 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 681.5
2019-03-09 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 327.5
2019-03-09 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-09 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-03-09 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-09 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-09 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-09 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-10 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-10 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-10 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-10 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-10 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-10 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 308.7 | 0
2019-03-10 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 300.1
2019-03-10 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-10 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 563.8
2019-03-10 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 44.8
2019-03-10 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 512.7
2019-03-10 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 285.6
2019-03-10 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-10 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-10 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-10 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-10 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-10 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-10 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-10 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-10 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-10 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-10 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-10 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 522.3
2019-03-11 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-11 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-11 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-11 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-11 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-11 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-11 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-11 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-11 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-11 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 224 | 0
2019-03-11 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 346.6 | 0
2019-03-11 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-12 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-12 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-12 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-12 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-12 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-12 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-12 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-12 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-12 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 303.3 | 0
2019-03-12 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-12 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 156
2019-03-12 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 96.1
2019-03-12 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 271.5
2019-03-12 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 176.5
2019-03-12 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 361.3
2019-03-12 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 523.1
2019-03-12 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-12 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-12 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-12 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-03-12 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 140.5 | 0
2019-03-12 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 478.5
2019-03-12 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-12 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-13 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-13 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-13 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-13 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-13 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-13 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-13 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-03-13 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-13 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-13 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-13 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 494.8 | 0
2019-03-13 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 351.7 | 0
2019-03-13 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 91.5 | 0
2019-03-13 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 33.6 | 0
2019-03-13 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 181.1
2019-03-13 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 73.6
2019-03-13 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 12.8
2019-03-13 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-13 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 174.2
2019-03-13 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 444.8 | 0
2019-03-13 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 158.6
2019-03-13 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 423
2019-03-13 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 599.8
2019-03-13 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-14 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-14 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-14 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-14 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-14 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-14 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-14 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-14 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-14 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 593.5 | 0
2019-03-14 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-14 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 588.3 | 0
2019-03-14 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 270.9 | 0
2019-03-14 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 96.6 | 0
2019-03-14 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 518.1
2019-03-14 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-14 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-14 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-14 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 180.7
2019-03-14 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 40.4 | 0
2019-03-14 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 659.4 | 0
2019-03-14 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 176.5 | 0
2019-03-14 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 442.5
2019-03-14 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 615.2
2019-03-14 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-15 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-15 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-15 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-15 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-15 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-15 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-15 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-15 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-15 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 519.8
2019-03-15 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-15 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-15 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-15 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-15 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-15 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 722.8
2019-03-15 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 626.2
2019-03-15 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 318.9
2019-03-15 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-15 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 75.7
2019-03-15 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 543.3 | 0
2019-03-15 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 400.7 | 0
2019-03-15 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 218.3
2019-03-15 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 354.5
2019-03-15 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 605.7
2019-03-16 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 369.4
2019-03-16 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 392
2019-03-16 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 279.9
2019-03-16 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 669
2019-03-16 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 596.3
2019-03-16 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 644.7
2019-03-16 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-16 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 715.1
2019-03-17 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-17 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 235.5
2019-03-17 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 8.4 | 0
2019-03-17 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 627.4 | 0
2019-03-17 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 347.2 | 0
2019-03-17 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 271.8
2019-03-17 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 607.9
2019-03-17 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 151.5
2019-03-18 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-18 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-18 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-18 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-18 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 643.5
2019-03-18 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 568.1
2019-03-18 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 26.5 | 0
2019-03-18 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 645.5 | 0
2019-03-18 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-18 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 624.6 | 0
2019-03-18 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 5.6 | 0 |  |  |  |  | Foreseen maintenance
2019-03-18 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-18 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-18 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-18 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-18 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-18 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 209.3 |  |  |  |  | Foreseen maintenance
2019-03-18 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 409.7 | 0 |  |  |  |  | Foreseen maintenance
2019-03-18 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 352.3 | 0 |  |  |  |  | Foreseen maintenance
2019-03-18 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-18 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-18 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 358.1 | 0 |  |  |  |  | Foreseen maintenance
2019-03-18 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-18 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 176 |  |  |  |  | Foreseen maintenance
2019-03-19 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-19 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-19 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-19 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-19 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-19 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-19 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 63.4 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 118 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-19 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-20 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-20 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-20 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-20 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-20 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-20 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 150.6 |  |  |  |  | Foreseen maintenance
2019-03-20 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 149.2 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 457.5 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 161.5 |  |  |  |  | Foreseen maintenance
2019-03-20 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-20 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-20 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-20 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 619 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 429.1 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-20 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 206 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 619 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 678 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 59 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-21 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 619 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 104 | 0 |  |  |  |  | Foreseen maintenance
2019-03-21 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 90.5 |  |  |  |  | Foreseen maintenance
2019-03-22 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-22 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-22 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-22 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-22 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 619 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 582.6 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 72.2 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-22 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-22 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-22 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-22 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-22 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 619 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 104 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-22 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 240.4 |  |  |  |  | Foreseen maintenance
2019-03-23 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-23 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-23 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-23 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-23 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-23 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-23 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 225.4 |  |  |  |  | Foreseen maintenance
2019-03-23 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-23 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-23 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 308.1 | 0 |  |  |  |  | Foreseen maintenance
2019-03-23 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 67.1 |  |  |  |  | Foreseen maintenance
2019-03-23 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 369.5 |  |  |  |  | Foreseen maintenance
2019-03-23 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-23 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-23 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-23 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-23 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-23 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-23 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 619 | 0 |  |  |  |  | Foreseen maintenance
2019-03-23 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 723 | 0 |  |  |  |  | Foreseen maintenance
2019-03-23 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 619 | 0 |  |  |  |  | Foreseen maintenance
2019-03-23 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-23 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-23 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-24 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-24 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 07 - 08 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 08 - 09 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 09 - 10 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 10 - 11 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 11 - 12 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 12 - 13 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 13 - 14 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 14 - 15 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 15 - 16 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 16 - 17 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 17 - 18 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-24 | 18 - 19 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 53.8 | 0 |  |  |  |  | Foreseen maintenance
2019-03-24 | 19 - 20 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 672.8 | 0 |  |  |  |  | Foreseen maintenance
2019-03-24 | 20 - 21 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 130.3 | 0 |  |  |  |  | Foreseen maintenance
2019-03-24 | 21 - 22 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 187.9 |  |  |  |  | Foreseen maintenance
2019-03-24 | 22 - 23 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-24 | 23 - 00 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 0 |  |  |  |  | Foreseen maintenance
2019-03-25 | 00 - 01 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-25 | 01 - 02 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-25 | 02 - 03 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-25 | 03 - 04 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-25 | 04 - 05 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-25 | 05 - 06 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-25 | 06 - 07 | n | j | https://umm.nordpoolgroup.com/#/messages/9e1726d3-7a7f-4412-8216-5e09b28e7c86/4 | 723 | 413 | 1136 |  |  | 0 | 300 | 0 | 0 | 0 | 413 |  |  |  |  | Foreseen maintenance
2019-03-25 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-25 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-25 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 229.4
2019-03-25 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-25 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-25 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-25 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-25 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-25 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-25 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-25 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-03-25 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-25 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-25 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 586.4 | 0
2019-03-25 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-25 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-25 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-26 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-26 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-26 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-26 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-26 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-26 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-26 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-26 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-26 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 86.2 | 0
2019-03-26 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-26 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 91.7 | 0
2019-03-26 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 215.2
2019-03-26 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 480
2019-03-26 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-26 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-26 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-26 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-26 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-26 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 297.5 | 0
2019-03-26 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-26 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-26 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-03-26 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-26 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-27 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-27 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-27 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-27 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-27 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-27 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-27 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-27 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-03-27 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-27 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-27 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-27 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-27 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-27 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-27 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-27 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-27 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-27 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-27 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-27 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-27 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-27 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-27 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-27 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-03-28 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-28 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-28 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-28 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-28 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-28 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-03-28 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-28 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-28 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-28 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-28 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-28 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-28 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 309.9 | 0
2019-03-28 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-28 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-28 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-28 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 549.8 | 0
2019-03-28 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-28 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-28 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-28 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-28 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-28 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-28 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-03-29 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-29 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-29 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-29 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-29 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 657.8
2019-03-29 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 38.8
2019-03-29 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 580.2 | 0
2019-03-29 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-29 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-29 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-03-29 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-29 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-29 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-29 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-29 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-29 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-29 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 362.5
2019-03-29 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 256.5 | 0
2019-03-29 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-29 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-29 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-29 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-29 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-29 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-30 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-03-30 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 565.7
2019-03-30 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 459.5
2019-03-30 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-03-30 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-03-30 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-03-30 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-30 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-30 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-03-30 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 518.7 | 0
2019-03-30 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 297.7 | 0
2019-03-30 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 321.3
2019-03-31 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 67.5 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 416.1 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 02 - 03 | [18 empty] | Change from winter time to summer time.
2019-03-31 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 101.8 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 312.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 350.3 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 380.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 284.6 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-03-31 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-01 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 247.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 178.1 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 77.9 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-02 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 223.9 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-03 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 413 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 413 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 413 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 413 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 413 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 413 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 186 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-04 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 242.7 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 413 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 413 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 413 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 247 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 81.9 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 413 | 846 |  |  | 0 | 300 | 300 | 300 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-05 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 221.9 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 357.2 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 183.4 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 127.9 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 292.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 147.3 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-06 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 317.1 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 7.1 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-07 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 67 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 33.6 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 425.3 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 272.9 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 1.1 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-08 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 236.8 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 329.1 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 391.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 398.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 261 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 390 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-09 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 110 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 214.2 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 37.4 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 338.1 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 241.4 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-10 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 236.6 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 145.9 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 116.2 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 133.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-11 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 195.6 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 47.7 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 159.2 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 27.7 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-12 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 6.2 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 318.4 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-13 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 178.8 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 300.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-14 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 337.4 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 281.6 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 55 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-15 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-16 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 157.3 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 5.5 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 419.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-17 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-18 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-19 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 93 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-19 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 130.7 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-19 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-19 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-19 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-19 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-19 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 416.4 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-19 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 362.9 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 129.5 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 398.2 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 112.7 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-19 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-20 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 34.9 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-20 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-20 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-20 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-20 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-20 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-20 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/47b49e75-8b47-40a4-9393-7ff83554bff0/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 138 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-20 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 246 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 423 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 274.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-20 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 199.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 228.1 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-21 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 367.6 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 232.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 386.8 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-22 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 360.6 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 376.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 338.8 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 401.4 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 245 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 389.8 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 229.2 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 148.2 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 432.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 387.6 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 342.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-23 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 140.4 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 192.6 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 406.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-24 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 111.1 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 149.9 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 58.9 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 179.6 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 57.7 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 97.6 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-25 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-26 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-26 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-26 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-26 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-26 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-26 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-26 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 304.3 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-26 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 190.5 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-26 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 346.6 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 343.2 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 355.6 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 433 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 322.7 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-27 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/04ed4205-af3e-44aa-b0d5-2b2f399b03e2/3 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity on the NorNed cable will be reduced due to maintenance in the Eemshaven region.
2019-04-28 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-28 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-28 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-28 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 11.1 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-28 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-28 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-28 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-28 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-28 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-28 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-28 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-29 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 116.6 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 61.3 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-04-30 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 19.9 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 294 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 260.2 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 20 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 237.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 343.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 275.8 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 122.4 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 19.6 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 254.7 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-01 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 386.5 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 373 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 294.1 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 299.7 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 33.7 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 424.1 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-02 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 285.1 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 333.9 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 382.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 300.5 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-03 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 287.7 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 148 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 28.6 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 340.3 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-04 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 221.6 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 20.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 204.6 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 237.8 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 144 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-05 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-06 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-06 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 76 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-06 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-06 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 140.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-06 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-06 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-06 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-06 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 156.2 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 394.7 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-06 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 311.8 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-07 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 247.6 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 38.3 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-08 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 268.1 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 239.9 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 44.3 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/2915f20c-b4ba-4a1d-9b67-9a7c304b4e10/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-05-09 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-09 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-09 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-09 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 294.4 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 324.6 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 19.9 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 269 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-10 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 325.7 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 293.3 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-11 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 134.9 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 32.3 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 233.1 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 398.8 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 259 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 123.4 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 218.8 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 432.8 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 422.3 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 93.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 66.1 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 163 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-12 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 240.6 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 306.1 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 312.9 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-13 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 212.6 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-14 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 406.4 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 112.1 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 72.8 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 283.7 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-15 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 364.1 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 43.3 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 396.8 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 56 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 3.8 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-16 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 63.3 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 349 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 323.2 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 232.3 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 192 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-17 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 404.5 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 214.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 130.7 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 364.8 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-18 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 98.5 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 235.2 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 134.3 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-19 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 433 | 433 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-20 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-21 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-21 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-21 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-21 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-21 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-21 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 373.3
2019-05-21 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-21 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-21 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-21 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-21 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-21 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-21 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-21 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-21 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-21 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 194.4 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-21 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 456.9 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-21 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 24.9 | 0
2019-05-21 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 643.9 | 0
2019-05-21 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-21 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-21 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-21 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 235.7 | 0
2019-05-21 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 38.6
2019-05-22 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-22 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-22 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-22 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-22 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-22 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-05-22 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-05-22 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-22 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-22 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-22 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-22 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-22 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-22 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 619 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-22 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 723 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-22 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 723 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-22 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 723 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-22 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-05-22 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-05-22 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-22 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-22 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-22 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-22 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 681 | 0
2019-05-23 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 62 | 0
2019-05-23 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-23 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-23 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-23 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 404.2
2019-05-23 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-05-23 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-23 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-05-23 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-05-23 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-23 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-05-23 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-23 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-23 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-23 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-23 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-23 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 317.8
2019-05-23 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 301.2 | 0
2019-05-23 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-23 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-23 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-23 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-23 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-23 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-24 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-24 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-05-24 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-24 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-24 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-24 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-24 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-05-24 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-24 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-24 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-24 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 355.2 | 0
2019-05-24 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-24 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-24 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 529.1
2019-05-24 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 459.9
2019-05-24 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-24 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 673
2019-05-24 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 54
2019-05-24 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 565 | 0
2019-05-24 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-24 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-24 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-24 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-24 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-25 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-25 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-05-25 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-25 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-25 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-25 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-25 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-25 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-25 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-25 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-25 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-25 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-25 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 430.9 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-25 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ef6cd3be-45fb-4e3a-96df-363147972726/11 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 723 |  |  |  |  | Failure on a filter in Eemshaven substation.
2019-05-25 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-25 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 642.1
2019-05-25 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 211.3
2019-05-25 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-25 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-05-25 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-25 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-25 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-25 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-25 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-26 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-05-26 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-26 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-26 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-26 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 9.7
2019-05-26 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 219.1
2019-05-26 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 406.8
2019-05-26 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 510.3
2019-05-26 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 532.6
2019-05-26 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-26 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-26 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-26 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 709.8
2019-05-26 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-26 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-26 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-26 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-26 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-26 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-26 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-05-26 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-26 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-26 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-26 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 154
2019-05-27 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515.5
2019-05-27 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-27 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-27 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-27 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-27 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-27 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-05-27 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-05-27 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-27 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-05-27 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-27 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-27 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-27 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-27 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-27 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 194.2
2019-05-27 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 625.7
2019-05-27 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 155.5
2019-05-27 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-05-27 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-27 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-27 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-27 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-27 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-05-28 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 187.3
2019-05-28 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 400.3
2019-05-28 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-28 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-28 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 240.5
2019-05-28 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-05-28 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 193.7 | 0
2019-05-28 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 146.8 | 0
2019-05-28 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 455.8 | 0
2019-05-28 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-28 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 161.9 | 0
2019-05-28 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 145.1
2019-05-29 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-29 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 201.6
2019-05-29 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 598.6
2019-05-29 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-29 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-29 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 513
2019-05-29 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 106 | 0
2019-05-29 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-29 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-29 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-29 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-29 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-29 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 719.3 | 0
2019-05-29 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 264.5 | 0
2019-05-29 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 147.9 | 0
2019-05-29 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-29 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 603.5 | 0
2019-05-29 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-29 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-29 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-29 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-29 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-29 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-05-29 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-30 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-05-30 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-30 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 373.1
2019-05-30 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 504.5
2019-05-30 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 474.4
2019-05-30 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 544.7
2019-05-30 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 569.3
2019-05-30 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 42.3
2019-05-30 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 106.9
2019-05-30 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 201.9
2019-05-30 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 161.5 | 0
2019-05-30 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 216.8 | 0
2019-05-30 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 548.8 | 0
2019-05-30 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 154 | 0
2019-05-30 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 36.2 | 0
2019-05-30 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 67.6
2019-05-30 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 178
2019-05-30 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 178.1
2019-05-30 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 122.1 | 0
2019-05-30 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 421.5 | 0
2019-05-30 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 338.6 | 0
2019-05-30 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 201.4 | 0
2019-05-30 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 660.3 | 0
2019-05-30 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 41.3 | 0
2019-05-31 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 577.7
2019-05-31 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-31 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-31 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-31 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-31 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-31 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-05-31 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-05-31 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-31 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-05-31 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-31 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-31 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-05-31 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-31 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 592.3
2019-05-31 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-05-31 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 561.2
2019-05-31 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-05-31 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-05-31 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-31 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-31 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-31 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-05-31 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 599.9 | 0
2019-06-01 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 19.1
2019-06-01 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 638.1
2019-06-01 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-01 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 690.8
2019-06-01 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 570.2
2019-06-01 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 562.2
2019-06-01 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 447.4
2019-06-01 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 180.1
2019-06-01 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 339.8
2019-06-01 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 179.4
2019-06-01 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 243.6
2019-06-01 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 450
2019-06-01 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 502.3
2019-06-01 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-01 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-01 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-01 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-01 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-01 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-06-01 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-06-01 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-01 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-01 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-06-01 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-02 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-06-02 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 533.7
2019-06-02 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-06-02 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-02 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 369.8
2019-06-02 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-02 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 341.5 | 0
2019-06-02 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 357.6 | 0
2019-06-02 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-02 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 201.3 | 0
2019-06-02 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 417.7
2019-06-03 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 530.6
2019-06-03 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 329.6
2019-06-03 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 316.5
2019-06-03 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 322.3
2019-06-03 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-03 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-06-03 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-03 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-06-03 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-03 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-03 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 283 | 0
2019-06-03 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-03 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-03 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-03 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-03 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-03 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-03 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-03 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-03 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-03 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-03 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-03 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-03 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-04 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-04 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-04 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-04 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-04 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-04 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-04 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-04 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-04 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-04 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-04 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-04 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-04 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 148.3 | 0
2019-06-04 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-04 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-04 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-04 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-06-04 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-04 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-04 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-04 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-04 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 674.2 | 0
2019-06-04 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 55.2 | 0
2019-06-04 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 36.4
2019-06-05 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-05 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 389 | 0
2019-06-05 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 541 | 0
2019-06-05 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 569.5 | 0
2019-06-05 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 288.6 | 0
2019-06-05 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 624.1 | 0
2019-06-05 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 422 | 0
2019-06-05 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-05 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-06 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-06-06 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 489.1
2019-06-06 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-06 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-06 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-06 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-06 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 572.3 | 0
2019-06-06 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-06 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-06 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-06 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 427.3 | 0
2019-06-06 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 559.7 | 0
2019-06-06 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 273.1 | 0
2019-06-06 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 259.1 | 0
2019-06-06 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 444.7 | 0
2019-06-06 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-06 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-06 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-06 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-06 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-06 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-06 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-06 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-06 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-06-07 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-07 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-07 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-07 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-07 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-07 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-07 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-07 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 701.2 | 0
2019-06-07 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 497.4 | 0
2019-06-08 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-08 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-09 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 556.8 | 0
2019-06-09 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 323.8 | 0
2019-06-09 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 664.3 | 0
2019-06-09 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 621.6 | 0
2019-06-09 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 650.8 | 0
2019-06-09 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 600.9 | 0
2019-06-09 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 9.8 | 0
2019-06-09 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 246.6
2019-06-09 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 222.5 | 0
2019-06-09 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-09 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 508.8 | 0
2019-06-10 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 210.7 | 0
2019-06-10 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 117.5 | 0
2019-06-10 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-10 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 42.8 | 0
2019-06-10 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 661.8 | 0
2019-06-10 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-10 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-10 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-10 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-10 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 332.8 | 0
2019-06-11 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 250.3 | 0
2019-06-11 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 51 | 0
2019-06-11 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 249.5 | 0
2019-06-11 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-11 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-11 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 530.1 | 0
2019-06-12 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-12 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 424.5 | 0
2019-06-13 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 600 | 0
2019-06-13 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 717.8 | 0
2019-06-13 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-06-13 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-13 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-13 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 154.8
2019-06-13 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-13 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-13 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-13 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-13 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-13 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-13 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 668.2 | 0
2019-06-14 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 150.3 | 0
2019-06-14 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 111.2 | 0
2019-06-14 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 447.2 | 0
2019-06-14 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 655.7 | 0
2019-06-14 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 346.4 | 0
2019-06-14 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-14 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-14 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-06-14 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-14 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 456.2 | 0
2019-06-15 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 650.8 | 0
2019-06-15 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 554.9 | 0
2019-06-15 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 683.3 | 0
2019-06-15 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 539.5 | 0
2019-06-15 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 387.8 | 0
2019-06-15 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-15 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-15 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 550.6 | 0
2019-06-16 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 412.5 | 0
2019-06-16 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 481.1 | 0
2019-06-16 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-16 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-16 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-16 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 357.1 | 0
2019-06-16 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-16 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-16 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-16 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-06-17 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-17 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-17 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 190.4 | 0
2019-06-17 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-17 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 190.3 | 0
2019-06-17 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 161.3 | 0
2019-06-17 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 363.4 | 0
2019-06-17 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 691.8 | 0
2019-06-17 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-17 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-18 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 630.6 | 0
2019-06-19 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-19 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-20 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 14.3 | 0
2019-06-20 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-20 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 444.8 | 0
2019-06-20 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 202.4 | 0
2019-06-20 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-20 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 416.3 | 0
2019-06-21 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 307.4 | 0
2019-06-21 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 474.8 | 0
2019-06-21 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 426.7 | 0
2019-06-21 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 350.8 | 0
2019-06-21 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-21 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-22 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-22 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 131 | 0
2019-06-22 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-22 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-22 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-22 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-22 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 71.5
2019-06-22 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-22 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 489.7 | 0
2019-06-22 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-22 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-22 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-22 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-22 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-22 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-22 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 102.2
2019-06-22 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 227.6
2019-06-22 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 70.4 | 0
2019-06-22 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 603 | 0
2019-06-22 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-22 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-22 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 325 | 0
2019-06-22 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-06-22 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-23 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 209.1
2019-06-23 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 74.2 | 0
2019-06-23 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 693.2 | 0
2019-06-23 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-23 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-23 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-23 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-23 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-23 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-23 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-23 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-23 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-06-23 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-23 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-23 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-23 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515.1
2019-06-23 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 34.3
2019-06-23 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 584.7 | 0
2019-06-23 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 699.3 | 0
2019-06-23 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-23 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-23 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 547.2 | 0
2019-06-23 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-23 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-24 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-24 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-24 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-24 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-24 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 610.1 | 0
2019-06-24 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-24 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-06-24 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-24 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-24 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 142 | 0
2019-06-24 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 15.8
2019-06-24 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-24 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 248.4 | 0
2019-06-24 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 360.9 | 0
2019-06-24 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 344.3 | 0
2019-06-24 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 589.2 | 0
2019-06-24 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 503.1 | 0
2019-06-24 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-24 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-24 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-24 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-24 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-24 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-24 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-25 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 312.3 | 0
2019-06-25 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 465.9 | 0
2019-06-25 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 712.2 | 0
2019-06-25 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 577.1 | 0
2019-06-25 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 34.7 | 0
2019-06-25 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 189.9 | 0
2019-06-25 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 315.8 | 0
2019-06-25 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 325.8 | 0
2019-06-25 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-25 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 328.1 | 0
2019-06-26 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-26 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-26 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-26 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-26 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-26 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-06-27 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 154.4 | 0
2019-06-27 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-27 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 202.1 | 0
2019-06-27 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-27 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 630.5 | 0
2019-06-28 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-28 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-29 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 652.2 | 0
2019-06-29 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 511.4 | 0
2019-06-29 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 301.1 | 0
2019-06-29 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-29 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 287.9 | 0
2019-06-29 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-29 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 431 | 0
2019-06-29 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-29 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 232.1 | 0
2019-06-29 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-29 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-29 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-29 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-29 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-29 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-29 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-29 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-29 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 210.2 | 0
2019-06-29 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-29 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-29 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-29 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-29 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-29 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-30 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 317.7 | 0
2019-06-30 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-30 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 481 | 0
2019-06-30 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 537.1 | 0
2019-06-30 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 252.8 | 0
2019-06-30 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-30 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 254.6
2019-06-30 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 623.2
2019-06-30 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 522.3
2019-06-30 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-06-30 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 621.1
2019-06-30 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 2.1
2019-06-30 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 616.9 | 0
2019-06-30 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 562.6 | 0
2019-06-30 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 582.9 | 0
2019-06-30 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 458.6 | 0
2019-06-30 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-06-30 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 177.2
2019-06-30 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 441.8 | 0
2019-06-30 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-30 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-30 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-30 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-06-30 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 130.6 | 0
2019-07-01 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 16.5 | 0
2019-07-01 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 122.3 | 0
2019-07-01 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 340.4 | 0
2019-07-01 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 716.1 | 0
2019-07-01 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 189.3 | 0
2019-07-01 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-01 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-01 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-01 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 56 | 0
2019-07-01 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 134.8 | 0
2019-07-01 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-01 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 647 | 0
2019-07-02 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-02 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-03 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-03 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-03 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-03 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 137.4 | 0
2019-07-03 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-03 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 626.6 | 0
2019-07-04 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 136.5 | 0
2019-07-04 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-04 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-04 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 4.4 | 0
2019-07-04 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 307 | 0
2019-07-04 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-04 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 177.8 | 0
2019-07-05 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-05 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-05 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-05 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-05 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-06 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-06 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-06 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-06 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-06 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-06 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 682.4 | 0
2019-07-06 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 63.4 | 0
2019-07-06 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-06 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 78.7 | 0
2019-07-06 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 115.4 | 0
2019-07-06 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 80.3 | 0
2019-07-06 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 110.3 | 0
2019-07-06 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 609.4 | 0
2019-07-06 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 649.5 | 0
2019-07-06 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 424.1 | 0
2019-07-06 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 70.5 | 0
2019-07-06 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-06 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 355.5 | 0
2019-07-06 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 374.5 | 0
2019-07-06 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-06 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-06 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-06 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-06 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-07 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-07 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-07 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-07 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-07 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-07 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 368.8 | 0
2019-07-07 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 484.2 | 0
2019-07-07 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 419.7 | 0
2019-07-07 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 354.5 | 0
2019-07-07 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 566.5 | 0
2019-07-07 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 304.1 | 0
2019-07-07 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-07 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 300.8
2019-07-07 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 334.3
2019-07-07 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-07 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 673.8
2019-07-07 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 367.8
2019-07-07 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 56.7 | 0
2019-07-07 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-07 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-07 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 276.4 | 0
2019-07-07 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-07 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-07 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-08 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-08 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 246.6 | 0
2019-07-08 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 194 | 0
2019-07-08 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-08 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-08 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 155.1 | 0
2019-07-09 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-09 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-09 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-09 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-09 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-09 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 605.1 | 0
2019-07-09 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 50 | 0
2019-07-09 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-09 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-09 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-09 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-09 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 542.1 | 0
2019-07-10 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-10 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-10 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 174.4 | 0
2019-07-10 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 313.2 | 0
2019-07-10 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-10 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 684.7 | 0
2019-07-11 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 501.4 | 0
2019-07-11 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-11 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 180.6 | 0
2019-07-12 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 91.8 | 0
2019-07-12 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 129.3 | 0
2019-07-12 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-12 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-13 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-13 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 239.9 | 0
2019-07-13 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 103.8 | 0
2019-07-13 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 405.7 | 0
2019-07-13 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-13 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 536.7 | 0
2019-07-13 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 72.5
2019-07-13 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 192
2019-07-13 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 201.3
2019-07-13 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-13 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-13 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-13 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 629.8 | 0
2019-07-14 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 10.8 | 0
2019-07-14 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 608.2
2019-07-14 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 230
2019-07-14 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 177.4
2019-07-14 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 53.2
2019-07-14 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 333.1
2019-07-14 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 319.8
2019-07-14 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 299.2 | 0
2019-07-14 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-14 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-14 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 243.6 | 0
2019-07-14 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-07-14 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-14 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-07-14 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-14 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-14 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 190.1
2019-07-14 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 428.9 | 0
2019-07-14 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-14 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-14 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-14 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 420.7 | 0
2019-07-14 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-14 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 446.6 | 0
2019-07-15 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-15 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-15 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-15 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-15 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-15 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-15 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 106 | 0
2019-07-15 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 182.7 | 0
2019-07-15 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 47.5 | 0
2019-07-15 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 362.5 | 0
2019-07-15 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-15 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 240.9 | 0
2019-07-16 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 295.3 | 0
2019-07-16 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-16 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-16 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-16 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-16 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-16 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 468.6 | 0
2019-07-16 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 553 | 0
2019-07-16 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-16 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 184.9 | 0
2019-07-16 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-16 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 348.2 | 0
2019-07-17 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-17 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-17 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-17 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-17 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-17 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-17 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 384.7 | 0
2019-07-18 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-18 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-07-18 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-18 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-18 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-07-18 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-18 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 261.4 | 0
2019-07-18 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-18 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-18 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-18 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-18 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-18 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-19 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 324.5
2019-07-19 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-19 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-19 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-19 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-07-19 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-07-19 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 135.6 | 0
2019-07-19 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-19 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-19 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-19 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-19 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-20 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-07-20 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-07-20 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-20 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-20 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-20 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-20 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-20 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-20 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-07-20 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-20 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 10.7 | 0
2019-07-20 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-21 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 391
2019-07-21 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 309.2
2019-07-21 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 170.7
2019-07-21 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 585
2019-07-21 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 478.3
2019-07-21 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-21 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-07-21 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-21 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-07-21 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-21 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-21 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-21 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-22 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-22 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-22 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 367.9
2019-07-22 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-22 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-22 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-07-22 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-22 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-22 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-22 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-22 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-22 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 550 | 0
2019-07-22 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 69
2019-07-22 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 688
2019-07-22 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-07-22 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-22 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 614.3 | 0
2019-07-22 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-22 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-22 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-22 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-22 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-22 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-22 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-23 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-23 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-23 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-23 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-07-23 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-23 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-23 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 171.7 | 0
2019-07-24 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-24 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 98.2
2019-07-24 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-07-24 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-24 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 356.9 | 0
2019-07-24 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 655.3 | 0
2019-07-24 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-24 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-25 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-25 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-25 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-07-25 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-25 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-26 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-26 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-26 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-26 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-26 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-26 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 655.1 | 0
2019-07-26 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-26 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 644.6 | 0
2019-07-27 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 25.6 | 0
2019-07-27 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 56.3
2019-07-27 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-07-27 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-27 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-27 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-27 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-27 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-27 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 398.9
2019-07-27 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-27 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-28 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-07-28 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-28 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 421.2
2019-07-28 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 137.7
2019-07-28 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-28 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-07-28 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-28 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-28 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-28 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-28 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-28 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-28 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-28 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-28 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-28 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-28 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-07-28 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-28 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-28 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-28 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-28 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-28 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 420.6 | 0
2019-07-28 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-29 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 266.9
2019-07-29 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 396.9
2019-07-29 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 337.2
2019-07-29 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 304.8
2019-07-29 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 494.5
2019-07-29 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-07-29 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-29 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-29 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-29 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 330.3
2019-07-29 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-29 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-29 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-30 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-30 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 436
2019-07-30 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-30 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-30 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-30 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 421.1
2019-07-30 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 197.9 | 0
2019-07-30 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-30 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-30 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-30 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-30 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-30 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-30 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-30 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-30 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-30 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-30 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 425.1 | 0
2019-07-30 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-30 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-30 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-30 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-30 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-30 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-31 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 241.3
2019-07-31 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-31 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-31 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-31 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-31 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-07-31 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-07-31 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-07-31 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-31 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-31 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 265.9 | 0
2019-07-31 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 538.9 | 0
2019-07-31 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 375.3 | 0
2019-07-31 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-07-31 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 115
2019-07-31 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 144.8
2019-07-31 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 252.5
2019-07-31 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-07-31 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-31 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-31 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-31 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-31 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-07-31 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-01 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-01 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-01 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 204.6
2019-08-01 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-01 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-01 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-08-01 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-01 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-01 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-01 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 647.9 | 0
2019-08-01 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 28.9 | 0
2019-08-01 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-01 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 579.4
2019-08-01 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 334.4
2019-08-01 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 65.3
2019-08-01 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-01 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-01 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-01 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-01 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-01 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-01 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-01 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-01 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-02 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-02 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-02 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-02 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-02 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-02 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-08-02 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-02 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-02 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-02 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-02 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-02 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-02 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 434.6 | 0
2019-08-02 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-02 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-02 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-02 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-02 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-08-02 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-02 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-02 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-02 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-02 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-02 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 406.1 | 0
2019-08-03 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-03 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 393.7
2019-08-03 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 359.8
2019-08-03 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 486.5
2019-08-03 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-03 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 474.1
2019-08-03 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-03 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-03 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 109.5
2019-08-03 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-03 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-03 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-03 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-03 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-03 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-03 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-03 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-03 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-03 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-03 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-03 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-03 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 520 | 0
2019-08-03 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-08-03 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-04 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 179
2019-08-04 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 672.3
2019-08-04 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 332.6
2019-08-04 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 569.8
2019-08-04 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-04 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-04 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 199.5 | 0
2019-08-04 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-04 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-04 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-04 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-05 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-05 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-08-05 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-05 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-05 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-05 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-08-05 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-05 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-08-05 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-05 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-05 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-05 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-05 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-05 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-08-05 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-05 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-08-05 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 629.9
2019-08-05 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 10.9
2019-08-05 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 509.4 | 0
2019-08-05 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-05 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-05 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-05 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-05 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-06 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-06 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-06 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-06 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-06 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-06 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-08-06 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-06 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-08-06 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-06 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-06 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-06 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-06 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-06 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-06 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-06 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-06 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 38 | 0
2019-08-06 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 657 | 0
2019-08-06 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-06 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-06 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-06 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-06 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-06 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 277.7 | 0
2019-08-07 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 226.7
2019-08-07 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-07 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-07 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-07 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-07 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-07 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 128.5
2019-08-07 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 490.5 | 0
2019-08-07 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-07 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-07 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-07 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-07 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 331.9 | 0
2019-08-07 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-07 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 512.5
2019-08-07 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-07 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619.9
2019-08-07 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0.9
2019-08-07 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 618.1 | 0
2019-08-07 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-07 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-07 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 605.5 | 0
2019-08-07 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-07 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-08 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-08-08 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-08-08 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-08 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 94 | 0
2019-08-08 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-08 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-08 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-08-08 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-08 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-08 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-08 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-08 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-08 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-09 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-08-09 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 529.4
2019-08-09 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-09 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-09 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-09 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-08-09 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-09 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-09 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-09 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-09 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 459.1 | 0
2019-08-09 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 570.5 | 0
2019-08-09 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 15.8 | 0
2019-08-09 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104.9 | 0
2019-08-09 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 479.9 | 0
2019-08-09 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-09 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-09 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-08-09 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-09 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-09 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 604.1 | 0
2019-08-09 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-09 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-09 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 507.5
2019-08-10 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 402.8
2019-08-10 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 593.7
2019-08-10 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 442.6
2019-08-10 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-10 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 394
2019-08-10 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 32.1 | 0
2019-08-10 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 406.5
2019-08-10 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-10 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 213.1 | 0
2019-08-11 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 405.9
2019-08-11 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 84.3
2019-08-11 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 207.5
2019-08-11 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 270.2
2019-08-11 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 302.9
2019-08-11 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 244.8
2019-08-11 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 283.2
2019-08-11 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 228.2
2019-08-11 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 683.4
2019-08-11 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 692.1
2019-08-11 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-11 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-11 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 620.2
2019-08-11 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 601.8
2019-08-11 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 477.1
2019-08-11 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 365.2
2019-08-11 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-11 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 363.8
2019-08-11 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-11 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-08-11 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-11 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-11 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-11 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-12 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-08-12 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 636.5
2019-08-12 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 563.5
2019-08-12 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-12 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-12 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-12 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 673.1
2019-08-12 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 54.1
2019-08-12 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-12 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-12 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-12 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-12 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-12 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-12 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-12 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 575.2
2019-08-12 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 41.8 | 0
2019-08-12 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 660.8 | 0
2019-08-12 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-12 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-12 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-12 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-12 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-12 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-13 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-13 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-13 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-13 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-13 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-13 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-13 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-13 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-13 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-13 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-13 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 484.7 | 0
2019-08-13 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-13 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-13 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-13 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-13 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-13 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-13 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 269.3 | 0
2019-08-13 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 235.8 | 0
2019-08-13 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-13 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-13 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-13 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-13 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-14 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-14 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-14 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-14 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-14 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-14 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 16.2
2019-08-14 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 602.8 | 0
2019-08-14 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-14 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-14 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 500.6 | 0
2019-08-14 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-14 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 369.1
2019-08-14 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-14 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-14 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-14 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-14 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-14 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-08-14 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-14 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-14 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-14 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-14 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-14 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-15 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-08-15 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-15 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-15 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-15 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-15 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-15 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-15 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 266.9
2019-08-15 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-15 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-15 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-15 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 701.3 | 0
2019-08-15 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 200.1 | 0
2019-08-15 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 289.1
2019-08-15 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-15 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-15 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 246.4
2019-08-15 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 47.7 | 0
2019-08-15 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-15 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-15 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-15 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 440.1 | 0
2019-08-15 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 59 | 0
2019-08-15 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-16 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-08-16 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-16 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-16 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-16 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-16 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 522.3
2019-08-16 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 96.7 | 0
2019-08-16 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 715.7 | 0
2019-08-16 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-16 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-16 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 202.4 | 0
2019-08-16 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-16 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 140.5
2019-08-16 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-16 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 259.1
2019-08-16 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-16 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-16 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-08-16 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-16 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-16 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-16 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-16 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 621.5 | 0
2019-08-16 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 2.5 | 0
2019-08-17 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 616.5
2019-08-17 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-17 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-17 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-17 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-17 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-17 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-17 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/ebf02559-3b3e-469a-b111-9010b14a2f0f/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 723 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-08-17 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/ebf02559-3b3e-469a-b111-9010b14a2f0f/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 723 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-08-17 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/ebf02559-3b3e-469a-b111-9010b14a2f0f/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 104 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-08-17 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/ebf02559-3b3e-469a-b111-9010b14a2f0f/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 190.8 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-08-17 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/ebf02559-3b3e-469a-b111-9010b14a2f0f/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 425.1 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-08-17 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/ebf02559-3b3e-469a-b111-9010b14a2f0f/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 723 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-08-17 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/ebf02559-3b3e-469a-b111-9010b14a2f0f/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 723 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-08-17 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/ebf02559-3b3e-469a-b111-9010b14a2f0f/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 723 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-08-17 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/ebf02559-3b3e-469a-b111-9010b14a2f0f/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 723 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-08-17 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/ebf02559-3b3e-469a-b111-9010b14a2f0f/1 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 723 |  |  |  |  | Reduction of the capacity NO2>NL to 0 MW from 07:00 until 17:00 due to maintenance in the NorNed - Eemshaven region.
2019-08-17 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 228.8
2019-08-17 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 26.3 | 0
2019-08-17 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 608.9 | 0
2019-08-17 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-17 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-17 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-17 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 639.7 | 0
2019-08-18 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-18 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-18 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-18 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-18 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 373.6 | 0
2019-08-18 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 538.4 | 0
2019-08-18 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-18 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 638.7 | 0
2019-08-18 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 19.7 | 0
2019-08-18 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 211.9
2019-08-18 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 15.7
2019-08-18 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 243.8
2019-08-18 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-18 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-18 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-18 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-18 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-18 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 536.6
2019-08-18 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 82.4 | 0
2019-08-18 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 701.4 | 0
2019-08-18 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-18 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-18 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-18 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-19 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 32.3
2019-08-19 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-19 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 513.5
2019-08-19 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-19 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-08-19 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-08-19 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-19 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-08-19 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-19 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-19 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 183.6
2019-08-19 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-19 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-19 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-19 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-19 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-19 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-19 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 141.9
2019-08-19 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 477.1 | 0
2019-08-19 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-19 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-19 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-19 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-19 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-20 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-20 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-20 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-20 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-20 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-20 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 440.1
2019-08-20 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 178.9 | 0
2019-08-20 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-20 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-21 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-21 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-21 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-21 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-21 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-21 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 160.8 | 0
2019-08-21 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-21 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-21 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-21 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 160.3 | 0
2019-08-21 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-21 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-22 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-22 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-22 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-22 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 50.7
2019-08-22 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 669.7
2019-08-22 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 270.4
2019-08-22 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 348.6 | 0
2019-08-22 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-22 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-22 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-22 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 212.6 | 0
2019-08-22 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-22 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-22 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-22 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-22 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-22 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 24.4 | 0
2019-08-22 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 643.4 | 0
2019-08-22 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-22 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-22 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-22 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-22 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-22 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 689.7 | 0
2019-08-23 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 70.7 | 0
2019-08-23 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-23 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-23 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-23 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 68.4
2019-08-23 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-23 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-23 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-23 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-23 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-23 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 531.6 | 0
2019-08-23 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 256.5 | 0
2019-08-23 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-23 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-23 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-23 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-23 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-23 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-23 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-23 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-23 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-23 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-23 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-23 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-24 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 591.4 | 0
2019-08-24 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-24 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-24 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-24 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-24 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-24 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 118.1 | 0
2019-08-24 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-24 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-24 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 503.7 | 0
2019-08-24 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 115.3
2019-08-24 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-24 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-24 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-24 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-24 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-24 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-08-24 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-24 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-24 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-24 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-24 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-24 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-24 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-25 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-08-25 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-25 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 385.2
2019-08-25 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 202.4
2019-08-25 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-25 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 82.7
2019-08-25 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 298.8
2019-08-25 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-25 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 413.5
2019-08-25 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 656
2019-08-25 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-25 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-25 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-25 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-25 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-25 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-08-25 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-08-25 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-25 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-08-25 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-25 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-25 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-25 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-25 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 428.4 | 0
2019-08-26 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-26 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-26 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-26 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-26 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-26 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-26 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-26 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 671.1 | 0
2019-08-27 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 521.2 | 0
2019-08-27 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 237 | 0
2019-08-27 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 380.9 | 0
2019-08-27 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 653.2 | 0
2019-08-27 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-27 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 613.1 | 0
2019-08-28 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-28 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 164.1 | 0
2019-08-29 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 89.4 | 0
2019-08-29 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 359 | 0
2019-08-29 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-29 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 500.1 | 0
2019-08-30 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-30 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-30 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-30 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 115 | 0
2019-08-30 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-30 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-31 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-31 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-31 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 234.1 | 0
2019-08-31 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 85.2
2019-08-31 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 371.8
2019-08-31 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 639.6
2019-08-31 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 20.6
2019-08-31 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-31 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-08-31 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-31 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 618.8 | 0
2019-08-31 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 154.9 | 0
2019-08-31 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-31 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-31 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-31 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-08-31 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-08-31 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-31 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-31 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-31 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-31 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-31 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-08-31 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-01 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-01 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-01 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-01 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-01 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-01 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-01 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-01 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 531.4
2019-09-01 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 700.5
2019-09-01 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 81.5
2019-09-01 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 39.5
2019-09-01 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-01 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-01 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-01 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 75.1
2019-09-01 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 371.6
2019-09-01 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 553.7
2019-09-01 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-01 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-09-01 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-01 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-01 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-01 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-01 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-02 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-02 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-02 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-02 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-02 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-02 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-02 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-03 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 236.2 | 0
2019-09-03 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-03 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-03 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-03 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-03 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-03 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 533.2 | 0
2019-09-03 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-03 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-03 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-03 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 716.1 | 0
2019-09-03 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 482.9 | 0
2019-09-03 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-03 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 22.1 | 0
2019-09-03 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 153.8 | 0
2019-09-03 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 223.1 | 0
2019-09-03 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 364.9 | 0
2019-09-03 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-03 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-03 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-03 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-03 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-03 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-03 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 529.1 | 0
2019-09-04 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-04 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-04 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-04 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-04 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 84.4
2019-09-04 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-04 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-09-04 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-04 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-04 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-04 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-04 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 301.2 | 0
2019-09-04 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-04 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-04 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-04 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-04 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-04 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-04 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-04 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-04 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-04 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-04 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 653 | 0
2019-09-04 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 34 | 0
2019-09-05 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 585
2019-09-05 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 409
2019-09-05 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-05 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 530.9
2019-09-05 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-05 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 562.6
2019-09-05 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 56.4 | 0
2019-09-05 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 675.4 | 0
2019-09-05 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-05 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 302.2 | 0
2019-09-05 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 114.2
2019-09-05 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 422.9
2019-09-05 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-05 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-05 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 412.4
2019-09-05 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-05 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-05 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-09-05 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-05 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-05 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-05 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-05 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-05 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 413.4 | 0
2019-09-06 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-06 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-06 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-06 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-06 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 144.5
2019-09-06 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-09-06 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-06 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-06 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-06 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-06 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-06 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-06 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-09-06 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-06 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-09-06 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-06 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-06 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-06 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-06 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-06 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-06 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-06 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-06 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 614.7 | 0
2019-09-07 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-07 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-07 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-07 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-07 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-07 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-07 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 387.2 | 0
2019-09-08 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 334.6 | 0
2019-09-08 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 161.7 | 0
2019-09-08 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 58.6 | 0
2019-09-08 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-08 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 565.6 | 0
2019-09-08 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 635.8 | 0
2019-09-08 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 658.6 | 0
2019-09-08 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 703 | 0
2019-09-08 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-08 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 495.2 | 0
2019-09-09 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-09 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-09 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-09 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-10 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-10 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-10 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-10 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-09-10 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-10 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 216.5 | 0
2019-09-10 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-10 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-10 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-10 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-10 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-10 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 112.2 | 0
2019-09-11 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 167.6 | 0
2019-09-11 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-11 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 466.6
2019-09-11 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-09-11 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-11 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 188.9 | 0
2019-09-11 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-11 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-11 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-11 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-11 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-11 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 393.9 | 0
2019-09-12 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 49.1 | 0
2019-09-12 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-12 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-12 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-12 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-12 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-12 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-09-13 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-13 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-13 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-13 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-13 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 288.4 | 0
2019-09-13 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-13 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-09-14 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-14 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-14 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-14 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 606.7 | 0
2019-09-15 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-15 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-16 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 197.1 | 0
2019-09-17 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 329.2 | 0
2019-09-17 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 642.9 | 0
2019-09-17 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-17 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 520.7 | 0
2019-09-18 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 218.3 | 0
2019-09-18 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 367.6 | 0
2019-09-18 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 416.6 | 0
2019-09-18 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 389.5 | 0
2019-09-18 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 676 | 0
2019-09-18 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 711.5 | 0
2019-09-18 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 699.2 | 0
2019-09-18 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-18 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-19 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 483.3 | 0
2019-09-20 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-20 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-21 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-09-21 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-21 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 597.6
2019-09-21 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-21 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-21 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-21 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-09-21 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-21 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-21 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-21 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-21 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-21 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 170.6
2019-09-21 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 380.1
2019-09-21 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-21 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-21 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 208.5
2019-09-21 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 410.5 | 0
2019-09-21 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-21 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-21 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-21 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-21 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-21 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-22 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-09-22 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-09-22 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-22 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-22 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-22 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 55
2019-09-22 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-22 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-09-22 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-22 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 171
2019-09-22 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-22 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 549
2019-09-22 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 391.2
2019-09-22 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-22 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-22 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-22 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-09-22 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-09-22 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-22 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-22 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-22 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-22 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-22 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 287.7 | 0
2019-09-23 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-23 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-23 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-23 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 424.3
2019-09-23 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-09-23 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-23 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-23 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 377.8 | 0
2019-09-24 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-24 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-24 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-24 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 137.2
2019-09-24 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 481.8 | 0
2019-09-24 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-24 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-25 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-25 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 6.7
2019-09-25 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 625.7
2019-09-25 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-25 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-09-25 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-25 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-09-25 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-25 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-26 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 64.7 | 0
2019-09-26 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 234.1
2019-09-26 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-26 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-09-26 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-26 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-26 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-26 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-26 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-27 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 83.3
2019-09-27 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 478.6
2019-09-27 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-27 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-27 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-27 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-09-27 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-09-27 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-27 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-27 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-27 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-27 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-27 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 448.5 | 0
2019-09-27 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 31.8
2019-09-27 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 650.8
2019-09-27 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 152.5
2019-09-27 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-27 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-27 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-27 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-27 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-27 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-27 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-27 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-09-28 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-28 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-28 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-28 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-28 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-28 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-28 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-28 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 578.2
2019-09-28 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 40.8 | 0
2019-09-28 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 659.8 | 0
2019-09-28 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 430.7 | 0
2019-09-28 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 62.2 | 0
2019-09-28 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-28 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 93.4
2019-09-28 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 164.6
2019-09-28 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 280.5
2019-09-28 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-09-28 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-28 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-09-28 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-28 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-09-28 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-28 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 307.1 | 0
2019-09-28 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 315.7 | 0
2019-09-29 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 290.5 | 0
2019-09-29 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 272 | 0
2019-09-29 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-09-29 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-29 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-29 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-29 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-29 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-29 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-29 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-29 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-09-29 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 434.8
2019-09-29 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-29 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-29 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-29 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-29 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-29 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-29 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-09-29 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-29 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-09-29 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 411.5 | 0
2019-09-29 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 366.7 | 0
2019-09-29 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-09-30 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-09-30 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-30 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-30 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-30 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-09-30 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 619 | 619 | 1238 |  |  | 0 | 100 | 100 | 100 | 0 | 619 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-09-30 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-01 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-02 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-03 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-04 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c28ad37e-69e4-495c-9cfe-0cc3b1f4f4ca/2 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Outage of 300 kV Kvinesdal-Feda, Feda 300 C, Feda 300 B, Feda FT1, Feda 300 BP2, Feda 300 HP1, Feda 300 HP2 and Feda-Eemshaven-2 (NorNed) due to removing of components from the old 300 kV Feda-Tonstad and 300 Feda-Kristiansand and 2-yearly maintenance work on interconnection NorNed between Norway and the Netherlands.
2019-10-05 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-10-05 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-05 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-05 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-05 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-05 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-05 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-06 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 449.7
2019-10-06 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-06 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-06 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-06 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-06 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-06 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-06 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-06 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-06 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 566.4
2019-10-06 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-06 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-06 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-06 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 420.7
2019-10-06 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-06 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-06 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-06 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 254
2019-10-06 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-06 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-06 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-06 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 325.8
2019-10-06 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-06 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-07 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-10-07 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-07 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-07 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-07 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-07 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-10-07 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-10-07 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-07 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 300.1 | 0
2019-10-07 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 577.4 | 0
2019-10-07 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 685.6 | 0
2019-10-07 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-07 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-07 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-07 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-07 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-07 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-07 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-07 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-07 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-07 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-07 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-10-07 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-10-07 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-08 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-08 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-08 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-08 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-08 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-08 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-08 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 521.6
2019-10-08 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 97.4 | 0
2019-10-08 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 716.4 | 0
2019-10-08 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-08 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 392.9 | 0
2019-10-08 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-08 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 149.8
2019-10-08 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 698.7
2019-10-08 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-08 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 718.5
2019-10-08 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 99.5
2019-10-08 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 519.5 | 0
2019-10-08 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 473.1 | 0
2019-10-08 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-08 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-08 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-10-08 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-08 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-09 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-09 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-09 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-09 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-09 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-09 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-09 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-10-09 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-09 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-09 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-09 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-09 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 122.1 | 0
2019-10-09 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-09 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 126.9
2019-10-09 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 176.4
2019-10-09 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 246.6
2019-10-09 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-10-09 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-09 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-09 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-09 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-09 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 435.4 | 0
2019-10-09 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 183.6
2019-10-09 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-10 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-10 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-10 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-10 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-10 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-10 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-10 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-10-10 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-10-10 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-10 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-10 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-10 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-10-10 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-10 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 680.2
2019-10-10 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-10 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-10 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-10-10 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-10 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-10 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-10 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-10 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-10-10 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-10 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 645.5
2019-10-11 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 26.5
2019-10-11 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 592.5 | 0
2019-10-11 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 140.1 | 0
2019-10-11 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-11 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 358.7 | 0
2019-10-11 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 229.6 | 0
2019-10-11 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 185.1
2019-10-11 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 254.6
2019-10-11 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-10-11 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-11 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-12 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-12 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-12 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-12 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-12 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-12 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-12 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-12 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 664
2019-10-12 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-10-12 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-12 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-12 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-12 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-12 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-12 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-12 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 230
2019-10-12 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 417.2
2019-10-12 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 201.8 | 0
2019-10-12 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-12 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-12 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-12 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-12 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-12 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 379.3
2019-10-13 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-13 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 0 | 0 | 0 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-14 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 192.5 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-15 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 426.5 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 363.7 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 86.9 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-16 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-17 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 122.6 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 309.7 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 55.4 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-18 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 418.8 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 393.7 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-19 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 87.6 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-20 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-21 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 84.4 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 24.4 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 47.2 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-22 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 309.2 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 298.5 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 320.5 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 65.3 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 299.1 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-23 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 198.7 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 99.9 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 150.4 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-24 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 216.8 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-25 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 396.3 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-26 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 340.4 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-27 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 216.7 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 33.3 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 313.2 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 315.4 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-28 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-29 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/5d333d56-7d34-4174-9737-cf16bf588530/4 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Fault in the station in Eemshaven.
2019-10-30 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-30 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 539.1
2019-10-30 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 442.9
2019-10-30 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-30 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-10-30 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-30 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-10-30 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-30 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-30 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-30 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-30 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 109.4 | 0
2019-10-30 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 435.3
2019-10-30 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 80.5
2019-10-30 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 143.6 | 0
2019-10-30 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-30 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-30 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-30 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-30 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-30 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-30 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-10-30 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-30 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-10-31 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-31 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 136.9
2019-10-31 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 154.9
2019-10-31 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 661.4
2019-10-31 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-31 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 572.4
2019-10-31 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 46.6 | 0
2019-10-31 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 665.6 | 0
2019-10-31 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-31 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-31 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-10-31 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 393.9
2019-10-31 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-10-31 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 259
2019-10-31 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 360 | 0
2019-10-31 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-31 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-31 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-31 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-31 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-31 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-10-31 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-10-31 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-10-31 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-01 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 190.8
2019-11-01 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 489.9
2019-11-01 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-01 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-01 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 121.7
2019-11-01 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-01 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 417.7
2019-11-02 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-02 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-02 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 375.8
2019-11-02 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-02 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 661.7
2019-11-02 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-02 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-03 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-03 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-03 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 195.2 | 0
2019-11-03 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-03 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-03 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-03 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-04 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-04 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-04 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-04 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-04 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-04 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-04 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-04 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-04 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-11-04 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-11-04 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-04 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-04 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-04 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 398.2 | 0
2019-11-04 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-04 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-04 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-04 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-04 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-04 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-04 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-11-04 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-04 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-04 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-05 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-05 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-05 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-05 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-05 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-05 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-05 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 572.9
2019-11-05 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 46.1 | 0
2019-11-05 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 665.1 | 0
2019-11-05 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-05 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-05 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-05 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 501.3
2019-11-06 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-06 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-06 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-06 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-06 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-06 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-06 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 254.7
2019-11-06 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 216.9 | 0
2019-11-06 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 301 | 0
2019-11-06 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 458.4 | 0
2019-11-06 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-06 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-07 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-07 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-07 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-07 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-07 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-07 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-07 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 212.2
2019-11-07 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 654.1
2019-11-07 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 582.6
2019-11-07 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 361.9
2019-11-07 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 434.2
2019-11-07 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 191.3
2019-11-07 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 380.5
2019-11-07 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 368.3
2019-11-07 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-07 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-07 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-07 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-07 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-07 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-07 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-07 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-07 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-07 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-08 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-08 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-08 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-08 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-08 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-08 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-08 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-08 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-08 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-08 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-08 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-08 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-08 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-08 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-08 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-08 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-08 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-08 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-08 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-08 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-08 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 518.3 | 0
2019-11-08 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-08 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-08 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 479.6
2019-11-09 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-09 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-09 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-09 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-09 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-09 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 329.9
2019-11-09 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-09 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-09 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-09 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-09 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-09 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-09 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-10 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 545.1
2019-11-10 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-10 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-10 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-10 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-10 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-10 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 384.8 | 0
2019-11-10 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 413.6 | 0
2019-11-10 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-10 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-10 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-11-10 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-10 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-11 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-11 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-11 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-11 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-11 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-11 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-11 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-11 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-11 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 154.7
2019-11-11 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-11 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-11 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-11 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-12 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-12 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-12 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-12 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-12 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-12 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-12 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-12 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-12 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-12 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-12 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-12 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-12 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-12 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 17.5
2019-11-12 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-12 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-12 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-12 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-12 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 661.4 | 0
2019-11-12 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 42.4 | 0
2019-11-12 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-12 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 134.7
2019-11-12 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-12 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-13 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-13 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-13 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-13 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-13 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-13 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-13 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 315.2
2019-11-13 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-13 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-13 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-13 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-13 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 97.5 | 0
2019-11-13 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 63.2 | 0
2019-11-13 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 499.4 | 0
2019-11-13 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 639.7 | 0
2019-11-13 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-13 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-13 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-13 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-13 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-13 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 151.6 | 0
2019-11-13 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-13 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 462.8
2019-11-13 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-14 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-14 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-14 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-14 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-14 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-14 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-14 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-14 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-14 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 78.3 | 0
2019-11-14 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-14 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-14 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-14 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-14 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 82.1 | 0
2019-11-14 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 514.5 | 0
2019-11-14 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 552.4 | 0
2019-11-14 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 288.4 | 0
2019-11-14 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 577.1 | 0
2019-11-14 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-14 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-14 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-14 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-14 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-14 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-15 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-15 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-15 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-15 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-15 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-15 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-15 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-15 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-15 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 173.9
2019-11-15 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 370.1
2019-11-15 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 289.9
2019-11-15 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-15 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 586.8
2019-11-15 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 42.6
2019-11-15 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 47.3 | 0
2019-11-15 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 666.3 | 0
2019-11-15 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-15 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-15 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-15 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 552.2 | 0
2019-11-15 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 54 | 0
2019-11-15 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-15 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-15 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-16 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-16 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-16 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-16 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-16 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-16 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-16 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 685.4
2019-11-16 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 180.7
2019-11-16 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 62.4 | 0
2019-11-16 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 618.1 | 0
2019-11-16 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-16 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-16 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 146.8
2019-11-16 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 116.8
2019-11-16 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-16 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-16 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 12 | 0
2019-11-16 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 469.6 | 0
2019-11-16 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-16 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-16 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-16 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-16 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-16 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-17 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-17 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-17 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-17 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-17 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-17 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-17 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-17 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-17 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-17 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-17 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-17 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-17 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-17 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-17 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 142.1
2019-11-17 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-17 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-17 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 394.5 | 0
2019-11-17 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-17 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-17 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-17 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-17 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-17 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-18 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-18 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-18 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-18 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-18 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-18 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-18 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 629.2
2019-11-18 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 88.5
2019-11-18 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 111.5 | 0
2019-11-18 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 722 | 0
2019-11-18 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-18 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-18 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-18 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-18 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-18 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-18 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-18 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-18 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-18 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-18 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 517.2
2019-11-18 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-18 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-18 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-19 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-19 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-19 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-19 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-19 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-19 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-19 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-19 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-19 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 280 | 0
2019-11-19 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 284.6 | 0
2019-11-19 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 244.6 | 0
2019-11-19 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 246.2 | 0
2019-11-19 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 417.6 | 0
2019-11-19 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-19 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-19 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-19 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-19 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-19 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-19 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-19 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-19 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-19 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-19 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 195.2
2019-11-20 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-20 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-20 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-20 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-20 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 534.4
2019-11-20 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 84.6 | 0
2019-11-20 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 703.6 | 0
2019-11-20 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-20 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 622.8 | 0
2019-11-20 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 3.8 | 0
2019-11-20 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 615.2
2019-11-20 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-21 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-21 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-21 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 710
2019-11-21 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-21 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-21 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 181.6
2019-11-21 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 437.4 | 0
2019-11-21 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-21 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-11-21 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-21 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 21.4
2019-11-21 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 638.8
2019-11-22 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-22 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-22 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-22 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-22 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-22 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-11-22 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-22 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-22 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-22 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-22 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-22 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-22 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-22 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-22 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-22 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-22 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-22 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-22 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 361.6 | 0
2019-11-22 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 257.4
2019-11-22 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-22 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-22 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-22 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-23 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-23 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-23 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 651.6
2019-11-23 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-23 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-23 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-23 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-23 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 391.8 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 24.1 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 45.7 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-23 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 338.4 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 27.6 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 2.4 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 382.7 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 121 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 127.4 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/3bd2ce50-049e-4611-b3aa-fb1f502e7258/2 | 0 | 723 | 723 |  |  | 0 | 700 | 700 | 700 | 0 | 0 |  |  |  |  | The capacity NO2->NL is reduced due to planned outage of the line Eemshaven-Meeden black on the Dutch side.
2019-11-24 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-11-24 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-24 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-24 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-24 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-25 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 245.5
2019-11-25 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-25 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-25 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-25 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-25 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-25 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-11-25 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-25 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 692.5 | 0
2019-11-25 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 73.5 | 0
2019-11-26 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 545.5
2019-11-26 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-26 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-26 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-26 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-26 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-11-26 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-26 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 711.5 | 0
2019-11-26 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-26 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-26 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-26 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-11-27 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-27 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-27 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-27 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-27 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-27 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-11-27 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-27 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-27 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-27 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-27 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-27 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 395.6 | 0
2019-11-27 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-27 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-27 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-27 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-27 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-27 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-27 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-27 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-27 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 258.9 | 0
2019-11-27 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 334.1
2019-11-27 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 265.3
2019-11-27 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 378
2019-11-28 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 74.1 | 0
2019-11-28 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 540.8
2019-11-28 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-28 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-28 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-28 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-28 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 104
2019-11-28 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 515 | 0
2019-11-28 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-28 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 219.8 | 0
2019-11-29 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 368.5 | 0
2019-11-29 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 173.1
2019-11-29 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 436.1
2019-11-29 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 337
2019-11-29 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 718.9
2019-11-29 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 245.9
2019-11-29 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 373.1 | 0
2019-11-29 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-29 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 313.9 | 0
2019-11-29 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-29 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 343.6 | 0
2019-11-29 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-29 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 573.6
2019-11-30 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-30 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 642.5
2019-11-30 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-30 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-30 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-30 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-11-30 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 492.6
2019-11-30 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 126.4 | 0
2019-11-30 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-30 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-30 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-30 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-30 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-30 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-30 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-30 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-30 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-30 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-30 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-30 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-30 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-11-30 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-11-30 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-11-30 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-01 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 212.1
2019-12-01 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-01 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-01 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-01 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-01 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-01 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-01 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-01 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 241.8
2019-12-01 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-01 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-12-01 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-01 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-01 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-01 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-01 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 604.6 | 0
2019-12-01 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-01 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-01 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-01 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-01 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-01 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 184.9 | 0
2019-12-01 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-01 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-12-02 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-02 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-02 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-02 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-02 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-02 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-12-02 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-12-02 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-02 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 666.6 | 0
2019-12-02 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-02 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 440.5 | 0
2019-12-02 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 316.4 | 0
2019-12-02 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-02 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 214.4 | 0
2019-12-02 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-02 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-02 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-02 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-02 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-02 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-02 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-02 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-02 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 596.5 | 0
2019-12-02 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-03 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 101.7
2019-12-03 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 720.7
2019-12-03 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 343
2019-12-03 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 108.6
2019-12-03 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-03 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-12-03 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 654 | 0
2019-12-03 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 611.1 | 0
2019-12-03 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-03 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 435 | 0
2019-12-03 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 333.6 | 0
2019-12-03 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 166
2019-12-03 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-04 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-04 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-04 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-04 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-04 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 692
2019-12-04 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 515
2019-12-04 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-12-04 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-04 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-12-04 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 224.9
2019-12-05 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-05 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-05 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 613.1
2019-12-05 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 722.1
2019-12-05 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-05 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 575.3
2019-12-05 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 43.7 | 0
2019-12-05 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 662.7 | 0
2019-12-05 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-05 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-05 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-05 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-05 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 266.2 | 0
2019-12-05 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 38.4 | 0
2019-12-05 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-05 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 543.8 | 0
2019-12-05 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-05 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-05 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-12-05 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 103.4 | 0
2019-12-05 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-05 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 156.7
2019-12-05 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 391.8
2019-12-05 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-06 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 662.4
2019-12-06 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-06 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-06 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-06 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-06 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-06 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-12-06 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-06 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 593.7 | 0
2019-12-06 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-06 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-06 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-06 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-06 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-06 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 652.5 | 0
2019-12-06 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-06 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-06 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-06 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-12-06 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 147.7
2019-12-06 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-06 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 677.9
2019-12-06 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-06 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-07 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-07 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-07 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-07 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-07 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-07 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-07 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-07 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-07 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 266.3
2019-12-07 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 352.7 | 0
2019-12-07 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 581.6 | 0
2019-12-07 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 302.9 | 0
2019-12-07 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-07 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 226.3
2019-12-07 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 326.9 | 0
2019-12-07 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 607 | 0
2019-12-07 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-07 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-07 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-07 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 616.4 | 0
2019-12-07 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 2.6
2019-12-07 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 621.6
2019-12-07 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 616
2019-12-07 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 264.1
2019-12-08 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 106.1
2019-12-08 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 470.4
2019-12-08 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 436.5
2019-12-08 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 211
2019-12-08 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 64.5 | 0
2019-12-08 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-12-08 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-08 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-08 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-12-08 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-08 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-12-08 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-08 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-09 | 00 - 01 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-09 | 01 - 02 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-09 | 02 - 03 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-09 | 03 - 04 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-09 | 04 - 05 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-09 | 05 - 06 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-09 | 06 - 07 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 619
2019-12-09 | 07 - 08 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2019-12-09 | 08 - 09 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 619 | 0
2019-12-09 | 09 - 10 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-09 | 10 - 11 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-09 | 11 - 12 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-09 | 12 - 13 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 673 | 0
2019-12-09 | 13 - 14 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 662.2 | 0
2019-12-09 | 14 - 15 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 62.2 | 0
2019-12-09 | 15 - 16 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 182.2 | 0
2019-12-09 | 16 - 17 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 570.4 | 0
2019-12-09 | 17 - 18 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 723 | 0
2019-12-09 | 18 - 19 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 104 | 0
2019-12-09 | 19 - 20 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 35.7
2019-12-09 | 20 - 21 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 654.7
2019-12-09 | 21 - 22 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-09 | 22 - 23 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-09 | 23 - 00 |  |  |  | 723 | 723 | 1446 |  |  | 0 | 0 | 0 | 0 | 0 | 723
2019-12-10 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-10 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-10 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-10 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-10 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-10 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure
2019-12-10 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-10 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-10 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 322.5 | 0 |  |  |  |  | Failure
2019-12-10 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 348.3 | 0 |  |  |  |  | Failure
2019-12-10 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 380.7 | 0 |  |  |  |  | Failure
2019-12-10 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-10 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-10 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-10 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-10 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-10 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-10 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 388 | 0 |  |  |  |  | Failure
2019-12-10 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 231 |  |  |  |  | Failure
2019-12-10 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-10 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-10 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-10 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-10 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-11 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-11 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-11 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-11 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-11 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-11 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-11 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-11 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 315.5 | 0 |  |  |  |  | Failure
2019-12-11 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-11 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-11 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-12 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-12 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-12 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-12 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-12 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-12 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-12 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-12 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 390.5 | 0 |  |  |  |  | Failure
2019-12-12 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-12 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-12 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-12 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-13 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-13 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-13 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-13 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-13 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-13 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-13 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-13 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure
2019-12-13 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-13 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-13 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-13 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-13 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-13 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-13 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-13 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-13 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 296.7 | 0 |  |  |  |  | Failure
2019-12-13 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-13 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-13 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-13 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 51 | 0 |  |  |  |  | Failure
2019-12-13 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-13 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 339 |  |  |  |  | Failure
2019-12-13 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 265.1 |  |  |  |  | Failure
2019-12-14 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 16.7 |  |  |  |  | Failure
2019-12-14 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 409.8 |  |  |  |  | Failure
2019-12-14 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 321.1 |  |  |  |  | Failure
2019-12-14 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-14 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-14 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-14 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-14 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 188.9 | 0 |  |  |  |  | Failure
2019-12-14 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 430.1 |  |  |  |  | Failure
2019-12-14 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-14 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 35.1 |  |  |  |  | Failure
2019-12-15 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 239.9 |  |  |  |  | Failure
2019-12-15 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 247.7 |  |  |  |  | Failure
2019-12-15 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 202.2 |  |  |  |  | Failure
2019-12-15 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 135.8 | 0 |  |  |  |  | Failure
2019-12-15 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-15 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure
2019-12-15 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-15 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-15 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-15 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-15 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 292.9 |  |  |  |  | Failure
2019-12-15 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-15 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 177.3 |  |  |  |  | Failure
2019-12-16 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 377.1 |  |  |  |  | Failure
2019-12-16 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-16 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-16 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-16 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-16 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-16 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-16 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 347.8 | 0 |  |  |  |  | Failure
2019-12-16 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-16 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-16 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-16 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 218.8 |  |  |  |  | Failure
2019-12-17 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure
2019-12-17 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-17 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-17 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-17 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-17 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 17.1 |  |  |  |  | Failure
2019-12-17 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 12 | 0 |  |  |  |  | Failure
2019-12-17 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-17 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-17 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-17 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 77.5 |  |  |  |  | Failure
2019-12-17 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-17 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-18 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-18 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-18 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-18 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-18 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-18 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-18 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure
2019-12-18 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-18 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-18 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 345.5 |  |  |  |  | Failure
2019-12-18 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-19 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-19 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-19 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-19 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-19 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-19 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-19 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-19 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 115.4 | 0 |  |  |  |  | Failure
2019-12-19 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-19 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-19 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-19 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-19 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-19 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-19 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 160 |  |  |  |  | Failure
2019-12-19 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-19 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-19 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-19 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-19 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-19 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-19 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-19 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-19 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-20 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-20 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-20 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-20 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-20 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-20 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-20 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-20 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-20 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 17 | 0 |  |  |  |  | Failure
2019-12-20 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-20 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 271 | 0 |  |  |  |  | Failure
2019-12-20 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-20 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 305.7 | 0 |  |  |  |  | Failure
2019-12-20 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-20 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-20 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 185.9 | 0 |  |  |  |  | Failure
2019-12-20 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 99.9 | 0 |  |  |  |  | Failure
2019-12-20 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-20 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 35.4 | 0 |  |  |  |  | Failure
2019-12-20 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-20 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-20 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 247.3 |  |  |  |  | Failure
2019-12-20 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-20 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 104.3 |  |  |  |  | Failure
2019-12-21 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 276.7 |  |  |  |  | Failure
2019-12-21 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-21 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-21 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-21 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 424.6 |  |  |  |  | Failure
2019-12-21 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 256.5 |  |  |  |  | Failure
2019-12-21 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-21 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 25 |  |  |  |  | Failure
2019-12-21 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-21 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-21 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-21 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-21 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 388.2 |  |  |  |  | Failure
2019-12-22 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 230.8 | 0 |  |  |  |  | Failure
2019-12-22 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure
2019-12-22 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 348.6 |  |  |  |  | Failure
2019-12-22 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 119 |  |  |  |  | Failure
2019-12-22 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-22 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-22 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-22 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-22 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-22 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-22 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-23 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-23 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-23 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-23 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 402.8 |  |  |  |  | Failure
2019-12-23 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 322 |  |  |  |  | Failure
2019-12-23 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-23 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-23 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-23 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-23 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 289.4 | 0 |  |  |  |  | Failure
2019-12-23 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-23 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-23 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-24 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 80.5 |  |  |  |  | Failure
2019-12-24 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0.1 |  |  |  |  | Failure
2019-12-24 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-24 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-24 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-24 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-24 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-24 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 387.7 |  |  |  |  | Failure
2019-12-24 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 278.5 |  |  |  |  | Failure
2019-12-24 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-24 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-24 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-24 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 363.5 |  |  |  |  | Failure
2019-12-24 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-24 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-24 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 395.7 |  |  |  |  | Failure
2019-12-24 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 50.5 | 0 |  |  |  |  | Failure
2019-12-24 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-24 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-24 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-24 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-24 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-24 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 237.2 |  |  |  |  | Failure
2019-12-24 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 328.6 |  |  |  |  | Failure
2019-12-25 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 128.1 |  |  |  |  | Failure
2019-12-25 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 220.2 |  |  |  |  | Failure
2019-12-25 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 136.3 | 0 |  |  |  |  | Failure
2019-12-25 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-25 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-25 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-25 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure
2019-12-25 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-25 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 96.9 |  |  |  |  | Failure
2019-12-25 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 249.6 |  |  |  |  | Failure
2019-12-26 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-26 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 395.1 |  |  |  |  | Failure
2019-12-26 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-26 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 335.3 |  |  |  |  | Failure
2019-12-26 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-26 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-26 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-26 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-26 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-26 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-26 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-26 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-26 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-27 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-27 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-27 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-27 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-27 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-27 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-27 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-27 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-27 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-27 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-27 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-27 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-27 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-27 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-27 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-27 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-27 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-27 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-27 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-27 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-27 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-27 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-27 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-27 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-28 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-28 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-28 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-28 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-28 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-28 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-28 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-28 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-28 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-28 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-28 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-28 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-28 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-28 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-28 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-28 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-28 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-28 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-28 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-28 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-28 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-28 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-28 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-28 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 186 | 0 |  |  |  |  | Failure
2019-12-29 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-29 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure
2019-12-29 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-29 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-29 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 0 |  |  |  |  | Failure
2019-12-29 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-29 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-29 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-29 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-29 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-29 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 359.3 | 0 |  |  |  |  | Failure
2019-12-29 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 259.7 |  |  |  |  | Failure
2019-12-30 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-30 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-30 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-30 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-30 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-30 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-30 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 186 |  |  |  |  | Failure
2019-12-30 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-30 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 144.6 | 0 |  |  |  |  | Failure
2019-12-30 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 21.5 |  |  |  |  | Failure
2019-12-30 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 130.8 |  |  |  |  | Failure
2019-12-31 | 00 - 01 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-31 | 01 - 02 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 433 |  |  |  |  | Failure
2019-12-31 | 02 - 03 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 0 | 185.8 |  |  |  |  | Failure
2019-12-31 | 03 - 04 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 230 | 0 |  |  |  |  | Failure
2019-12-31 | 04 - 05 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 372.6 | 0 |  |  |  |  | Failure
2019-12-31 | 05 - 06 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 397.9 | 0 |  |  |  |  | Failure
2019-12-31 | 06 - 07 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 123.3 | 0 |  |  |  |  | Failure
2019-12-31 | 07 - 08 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 369.1 | 0 |  |  |  |  | Failure
2019-12-31 | 08 - 09 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 09 - 10 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 10 - 11 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 11 - 12 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 12 - 13 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 13 - 14 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 14 - 15 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 15 - 16 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 16 - 17 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 17 - 18 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 18 - 19 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 19 - 20 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 20 - 21 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 21 - 22 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 22 - 23 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure
2019-12-31 | 23 - 00 | n | n | https://umm.nordpoolgroup.com/#/messages/c7d83d27-52f8-481a-a4de-43b165b400c5/1 en https://umm.nordpoolgroup.com/#/messages/c71b5a5f-8732-428e-b4cd-86ec5604b104/1 | 433 | 433 | 866 |  |  | 0 | 281 | 281 | 281 | 433 | 0 |  |  |  |  | Failure

## Tabel 4 Bronnen
Tabel 4 - Gebruikte bronnen
| Day ahead capacity: | https://www.nordpoolgroup.com/globalassets/marketdata-excel-files/market-coupling-capacities_2019_hourly.xls
| Intraday initial capacity: | *1)
| Day ahead flow: | https://www.nordpoolgroup.com/globalassets/marketdata-excel-files/market-coupling-flow_2019_hourly.xls
| Intraday flow: | *1)
| UMM's: | https://umm.nordpoolgroup.com/#/messages?publicationDate=custom&publicationDateStart=2018-12-01&publicationDateStop=2019-12-31&eventDate=custom&eventDateStart=2018-12-01&eventDateStop=2019-12-31&connections=NL-NO2&connections=NO2-NL
*1) - as from the go-live of the European Cross-Border Intraday (XBID) Solution on June 12, 2018 the (ELBAS) data for intraday is no longer available via the website of Nordpoolgroup.
The absence of this data has no impact on the proposal of TenneT as the maximum malus is already proposed for the year 2019.