## Asset list DH companies
Asset Life Assessment DH companies ¦ Two-Step Methodology: Technical Lifetime -> Economic Lifetime
IDENTIFICATION |  |  |  | STEP 1: TECHNICAL LIFETIME | [8 empty] | STEP 2: ECONOMIC LIFETIME |  |  |  | Sweden |  |  |  |  | PlanEnergi remark
RAR Cat. | ID | Asset Category / Component | Description | Baseline Lifetime [yr] | ETC Range [yr] | Source | Asset Composition | ETC Compatibility | Step 1 Notes | Use Component Assessment (if available) | Comp. Wtd Avg [yr] | Technical Lifetime [yr] | Degradation Risk | Policy / Stranding Risk | Step 2 Notes | Economic Lifetime [yr] | Tech Lifetime Sweden | Economic Lifetime Sweden | Source | Economic Lifetime Germany | Source
I. Intangible Fixed Assets
I.1 Software and Licences
I | I.1.1 | Operations management / ERP | Enterprise resource planning and customer management software incl. server hardware and licences. | 8 | - | PlanEnergi/BPC (Engineering judgement) | 2 | N | Life driven by vendor support cycles and functional obsolescence. | No | 0 | 8 | 1 | 0 | MEDIUM technical risk: IT hardware cycles. LOW policy risk. | 5
I | I.1.2 | GIS and asset management software | Geographic information system and asset register software for network mapping and maintenance planning. | 10 | - | PlanEnergi/BPC (Engineering judgement) | 2 | N | GIS data migration costs extend practical economic life vs ERP. | No | 0 | 10 | 1 | 0 | GIS data often outlives the platform; migration options extend useful life. | 8
I | I.1.3 | R&D and development costs | Capitalised development and design costs for new heat systems, if separately identified in the RAB. | - | - | Accounting policy | N | N | Life = useful life of resulting asset. ACM/RJ determination required. | No | 0 | - | N | N | Not a standalone depreciable asset in all jurisdictions. | -
II.a. Heat Networks
II.a.1 Transport and Distribution Pipes
II.a | II.a.1.1 | Transmission pipes | Pre-insulated steel carrier pipe DN200+, >100°C forward. Long-distance backbone. incl. pipes, fittings, welded joints. | 45 | 30-60 | ETC 08 Ch. #3.1 | 0 | 0 | Physical/technical lifetime much higher. Heavily corrected for insulation degradation etc. | No | 0 | 45 | 0 | 0 | Insulation degradation, starts operating less effectively. Common book keeping practice | 45 | min. 30 | 80-100 | The technical life time is a requirement from the standard SS-EN 253 underhållshandboken för fjärrvärmedistribution p. 23 | 40 | Technology Data Catalogue KEA BW (partly based on ETC)
II.a | II.a.1.2 | Primary distribution pipes | Pre-insulated steel carrier pipe (usually DN50-200 operating at 65-85°C). From source to neighbourhood distribution point. | 45 | 30-60 | ETC 08 Ch. #3.2 | 1 | 0 | Same as transmission pipe. Physical lifetime identical. | No | 0 | 45 | 0 | 0 | Insulation degradation, starts operating less effectively. Common book keeping practice | 45 | min. 30 | 80-100 | The technical life time is a requirement from the standard SS-EN 253 underhållshandboken för fjärrvärmedistribution p. 23 | 40 | Technology Data Catalogue KEA BW (partly based on ETC)
II.a | II.a.1.3 | Secondary distribution pipes | Pre-insulated carrier pipe (usually DN32-150 operating at 65-85°C). From distribution point to local area. | 45 | 30-60 | ETC 08 Ch. #3.3 | 1 | 0 | Same assessment. Smaller diameter, equal lifetime. | No | 0 | 45 | 0 | 0 | Insulation degradation, starts operating less effectively. Common book keeping practice | 45 | min. 30 | 80-100 | The technical life time is a requirement from the standard SS-EN 253 underhållshandboken för fjärrvärmedistribution p. 23 | 40 | Technology Data Catalogue KEA BW (partly based on ETC)
II.a | II.a.1.4 | Service connections / house connections | Pre-insulated PEX or steel pipe DN20-50 from disitribution grid to building boundary. Incl. isolation valve and house connection box. | 30 | - | PlanEnergi/BPC (Engineering judgement) | 0 | N | PEX technical life ~30yr. No ETC range entry. | No | 0 | 30 | 0 | 1 | MEDIUM policy risk: building-level HPs and renovation may render connections redundant before technical end-of-life. | 25 |  | 30-60 | Flexibla ledningar (medierör av stål och koppar) underhållshandboken för fjärrvärmedistribution p. 23 | 40 | Technology Data Catalogue KEA BW (partly based on ETC)
II.a | II.a.1.5 | Low temperature ambient loop pipes | Low-temperature ambient loop for 5th gen DHC (usually operating at up to 25°C). Predominantly plastics (PE/HDPE/PEX) at low pressure and temperature. | 75 | - | PlanEnergi/BPC (Engineering judgement) | 0 | N | Technical life well above Bcw cap. Very low operating stress. | No | 0 | 75 | 0 | 0 | No policy risk for the pipe itself. Bcw cap is the binding constraint. | 60
II.a.2 Heat Transfer Stations and Substations
II.a | II.a.2.1 | Area-level heat transfer station / substation | Intermediate station transferring heat between transmission and distribution. Incl. plate heat exchanger, pumps, expansion vessel, controls, enclosure. | 25 | - | PlanEnergi/BPC (Engineering judgement) | 2 | N | Equipment-heavy: pumps+controls ~55% of cost at 15yr. | Yes | 26.25 | 26.25 | 1 | 0 | MEDIUM technical risk: pumps and controls require mid-life replacement. | 20
II.a.3 Pumping Stations
II.a | II.a.3.1 | Main network circulation pumping station | Central pump sets, motors, VFDs, manifold pipework. Incl. control panel and automation. Excl. building (see II.a.6.1). | 20 | - | PlanEnergi/BPC (Engineering judgement) | 2 | N | Pump-dominated | Yes | 25 | 25 | 1 | 0 | MEDIUM technical risk: pumps replaced at ~15yr but structure lasts longer. | 20
II.a | II.a.3.2 | Booster pump station | Smaller intermediate pump station for pressure maintenance in remote grid zones. Incl. pump set, VFD, controls and enclosure. | 20 | - | PlanEnergi/BPC (Engineering judgement) | 2 | N | Same assessment as main pumping station. | No | 0 | 20 | 1 | 0 |  | 20
II.a.4 Valves and Control Equipment
II.a | II.a.4.1 | Network isolation and control valves | Gate, butterfly or ball valves DN50-600 for network sectoring. Incl. valve chamber and actuators where applicable. | 25 | - | PlanEnergi/BPC (Engineering judgement) | 1 | N | Manual valves 30yr; actuated valves 15yr. (actuators ~35% of cost). | No | 0 | 25 | 1 | 0 | MEDIUM technical risk: actuator electronics drive earlier economic life. | 20
II.a | II.a.4.2 | Pressure regulation and expansion equipment | Pressure-reducing valves, expansion vessels and safety valves. | 20 | - | PlanEnergi/BPC (Engineering judgement) | 2 | N | Dynamic loading and membrane wear. Shorter than isolation valves. | No | 0 | 20 | 1 | 0 |  | 15
II.a.5 Metering and Instrumentation
II.a | II.a.5.1 | District-level metering and instrumentation | Flow meters, pressure transducers and temperature sensors at transmission/district boundary. Incl. remote reading. | 18 | - | PlanEnergi/BPC (Engineering judgement) | 2 | N | Electronic transmitters shorter than mechanical sensors. | No | 0 | 18 | 1 | 0 |  | 15
II.a | II.a.5.2 | SCADA and network control system | Supervisory control and data acquisition for network monitoring and pump control. Incl. servers, software, communication and RTUs. | 12 | - | PlanEnergi/BPC (Engineering judgement) | 1 | N | Hardware-dominated. Vendor support cycles and software obsolescence drive life. | No | 0 | 12 | 2 | 1 | HIGH technical risk: IT hardware obsolescence. MEDIUM policy risk: cybersecurity requirements may force earlier upgrades. | 10
II.a.6 Buildings and Civil Works
II.a | II.a.6.1 | Utility and Equipment Buildings | Lightweight utility and equipment building (typically a steel-frame structure, possibly prefabricated) housing technical equipment such as pumps and booster units. | 40 | - | PlanEnergi/BPC (Engineering judgement) | 0 | N | Civil structure dominated. No equipment intensity concern. | No | 0 | 40 | 0 | 0 |  | 35
II.a | II.a.6.2 | Operations and Administration Building | Permanent concrete or masonry building housing operational, administrative and process-related functions (e.g. control rooms, workshops, offices, boiler houses and heat production equipment). | 50 | - | PlanEnergi/BPC (Engineering judgement) | 0 | N | Civil structure dominated. No equipment intensity concern. | No | 0 | 50 | 0 | 0 |  | 45 |  |  |  | 50 | AfA-table "Energie- und Wasserwirtschaft"
II.a | II.a.6.3 | Civil works - excavation, reinstatement and crossings | Excavation, backfill, road reinstatement and HDD for pipe installation. Typically embedded in pipe asset cost. | 45 | 30-60 | ETC 008 Ch. #3.1-3.4 | 0 | 1 | Civil component of pipe investment. Technical life = pipe life. | No | 0 | 45 | 1 | 0 | Follows life of corresponding pipe. | 45 |  |  |  | 50 | AfA-table "Energie- und Wasserwirtschaft"
II.b. Heat Production and Storage
II.b.1 Heat only Boilers, incl. Backup and Peak Heat Production
II.b | II.b.1.1 | Gas boiler - peak / backup | Natural gas-fired hot water boiler. Incl. burner, heat exchanger vessel, controls and safety systems. | 25 | 20-30 | ETC 0018 Ch. #44 | 1 | 0 | Burner+controls ~30% of cost at 25yr. | No | 0 | 25 | 0 | 2 | HIGH policy risk: gas phase-out post-2035. Economic life shortened to 20yr. | 20 |  |  |  | 25 | KWW-Katalog (based on ETC).
II.b | II.b.1.2 | Electric boiler - peak / backup | Electric resistance or electrode boiler. Incl. power supply connection and controls. Typically connected at mid (or low) voltage. | 20 | 20-25 | ETC 0018 Ch. #41 | 1 | 0 | Simple technology. Low equipment intensity. | Yes | 23.3333 | 23.3333 | 0 | 0 | LOW risk on both axes. | 20
II.b | II.b.1.3 | Wood chip boiler - standalone production unit | Biomass-fired hot water boiler (wood chips). Incl. furnace, heat exchanger, filtration, pumps and controls. Excludes common plant infrastructure. | 25 | 20-30 | ETC 0018 Ch. #09a | 1 | 0 | Component analysis (RAR prod. unit 1 - wood chip boiler): wtd avg = 26yr confirms ETC 25yr. | No | 0 | 25 | 1 | 1 | MEDIUM technical risk: inspection-based maintenance. MEDIUM policy risk: biomass sustainability. | 20
II.b.2 Combined Heat and Power (CHP)
II.b | II.b.2.1 | Gas engine CHP | Reciprocating gas engine with heat recovery. Incl. generator, heat recovery unit, cooling system and controls. | 25 | 20-30 | ETC 0018 Ch. #06 | 1 | 0 | Engine overhaul cycles at 8-10yr. ETC 25yr with major overhaul assumption. | No | 0 | 25 | 1 | 2 | MEDIUM technical risk: overhaul economics valid. HIGH policy risk: gas phase-out. | 20 |  |  |  | 15 | KWW-Katalog (based on VDI Blatt 2067).
II.b | II.b.2.2 | Gas turbine Combined Cycle | Gas turbine (combined cycle) with heat recovery. Incl. turbine, generator, HRSG and auxiliaries. | 25 | 20-30 | ETC 0018 Ch. #04/#05 | 1 | 0 | Turbine overhaul at 10-15yr. Same ETC approach. | No | 0 | 25 | 1 | 2 | Same as gas engine CHP. | 20
II.b | II.b.2.3 | Waste-to-Energy (WtE) CHP | Municipal solid waste combustion with steam cycle and heat extraction. Incl. grate/boiler, flue gas treatment, turbine and heat exchanger. | 25 | 20-30 | ETC 0018 Ch. #08 | 1 | 0 |  | No | 0 | 25 | 1 | 1 | MEDIUM technical risk: boiler pressure parts may need replacement. MEDIUM policy risk (increasing recycling rates). | 25
II.b | II.b.2.4 | Biomass CHP (wood chips / pellets / straw) | Biomass-fired boiler with steam turbine or back-pressure extraction. Incl. boiler, fuel handling, turbine and condenser. | 25 | 20-30 | ETC 0018 Ch. #09a/b/c | 1 | 0 | Component analysis (RAR prod. unit 3 - wood chip CHP): wtd avg = 26yr confirms ETC 25yr. Same range for smaller scale (ORC). | No | 0 | 25 | 1 | 1 | MEDIUM technical risk: overhaul-based. MEDIUM policy risk: biomass sustainability regulations. | 25 |  |  |  | 25-28 | KWW-Katalog (based on ETC).
II.b.3 Heat Pumps
> Air/Water Heat Pump (A/W HP)
II.b | II.b.3.1a | A/W HP - commercial type (<=5 MW, factory unit) | Standardised factory-assembled compression HP. All refrigerant components pre-assembled. Not overhauled - unit replaced at end of life. | 25 | 15-40 | ETC 0018 Ch. #40 | 1 | 1 | ETC 25yr biased toward industrial type. Commercial units NOT overhauled: effective technical life = 15yr. | Yes | 20.4348 | 20.4348 | 2 | 1 | HIGH technical risk: no overhaul access; compressor replacement = new unit. MEDIUM policy risk: refrigerant regulations. | 15 |  |  |  | 25 | KWW-Katalog (based on ETC).
II.b | II.b.3.1b | A/W HP - industrial type (>5 MW) | Custom-built large-scale compression HP. Industrial refrigeration components maintained via scheduled overhaul. | 25 | 15-40 | ETC 0018 Ch. #40 | 1 | 0 | ETC 25yr applies with overhaul assumption. Custom design enables overhaul economics. | Yes | 21.3043 | 21.3043 | 1 | 1 | MEDIUM technical risk: overhaul-based (8-10yr cycles). MEDIUM policy risk: refrigerant regulations. | 20 |  |  |  | 25 | KWW-Katalog (based on ETC).
> Water/Water Heat Pump (W/W HP)
II.b | II.b.3.2a | W/W HP - commercial type | Factory unit compression HP using ground/aquifer/surface water. All refrigerant components pre-assembled. No overhauls. | 25 | 15-40 | ETC 0018 Ch. #40 | 1 | 1 | Same split rationale as ASHP. Component analysis incl. WKO wells (40yr) gives wtd avg = 24yr, but wells skew upward. | Yes | 23.7931 | 23.7931 | 2 | 1 | HIGH technical risk: no overhaul access. MEDIUM policy risk: Refrigerant regulation and exploration of heat source. | 15 |  |  |  | 25 | KWW-Katalog (based on ETC).
II.b | II.b.3.2b | W/W HP - industrial type | Custom large-scale compression HP with water heat source. Overhaul-based maintenance on industrial refrigeration components. | 25 | 15-40 | ETC 0018 Ch. #40 | 1 | 0 | Component analysis wells-inclusive: 24yr. HP unit with overhauls: 25yr. | Yes | 24.4828 | 24.4828 | 1 | 1 | MEDIUM policy risk: Refrigerant regulation and exploration of heat source. | 20 |  |  |  | 25 | KWW-Katalog (based on ETC).
II.b | II.b.3.3 | Seawater / surface water HP | Compression HP using sea, lake or river water. Incl. compressor unit, water intake/discharge and heat exchangers. | 25 | 15-40 | ETC 0018 Ch. #40 | 1 | 0 | Water intake civil works: separate asset. | No | 0 | 25 | 1 | 1 | MEDIUM policy risk: Refrigerant regulation and exploration of heat source. | 20 | 55 |  | Sea water HP Ropsten 1&2 in Stockholm were installed 1988 and is expected to run another 15 years. Niras, System og teknologi, 2021, p.25 | 25 | KWW-Katalog (based on ETC).
II.b | II.b.3.4 | Waste heat / industrial excess heat HP | Compression HP recovering low-grade heat from industrial processes, data centres or wastewater. | 25 | 15-40 | ETC 0018 Ch. #40 | 1 | 0 | Same HP lifetime rationale. Primary-side industrial process piping excluded from DH RAB. | No | 0 | 25 | 1 | 2 | HIGH policy/stranding risk: Refrigerant regulations. Additionally, the future of an industrial heat source is not determined by the utility company. | 15 |  |  |  | 20 | KWW-Katalog (based on ETC).
II.b.4 Geothermal
II.b | II.b.4.1 | Deep geothermal doublet (incl. surface HP) | Deep geothermal doublet (1,200-2,000 m) with downhole pumps and surface HP. Incl. well casing, downhole equipment and surface interconnecting pipework. | 25 | 25-30 | ETC 0018 Ch. #45.1-45.3 | 1 | 0 | Well casings: ~40yr. Downhole pumps: 10-15yr. Surface HP: 15-25yr. | No | 0 | 25 | 1 | 0 | MEDIUM technical risk: downhole pump replacement at 10-15yr is expensive. LOW policy risk (renewable heat). Stranding risk of deep geothermal is very high initially, but minimized at the time of investment decision. | 25 |  |  |  | 30 | KWW-Katalog (German references).
II.b.5 Solar and Waste Heat Recovery
II.b | II.b.5.1 | Solar district heating - collector field | Large-scale flat-plate or evacuated-tube solar collector array with primary circuit and heat exchangers. | 30 | 25-35 | ETC 0018 Ch. #46 | 0 | 0 | ETC 30 yr validated by Danish large-scale installations. | No | 0 | 30 | 1 | 0 | Proven technology. Economic lifetime lowered due to expected declining performance over time. | 20 |  |  |  | 25 | KWW-Katalog (based on ETC).
II.b | II.b.5.2 | Waste heat recovery installation | Heat exchanger capturing industrial excess heat or data-centre heat. Incl. primary-side heat exchanger, secondary pumps and controls. | 25 | - | PlanEnergi/BPC (Engineering judgement) | 1 | N |  | No | 0 | 25 | 1 | 2 | Considerable stranding risk, if the heat source is depleted/ends (e.g. processes are adapted or company shut down). | 15
II.b | II.b.5.3 | TEO broninstallatie (Thermische Energie uit Oppervlaktewater) | Heat exchanger system capturing thermal energy from surface water (river, lake or canal). Includes filters, plate/tube heat exchanger, civil intake works and connecting pipework. | 30 | - | PlanEnergi/BPC (Engineering judgement) | 1 | N |  | Yes | 26.0714 | 26.0714 | 1 | 0 | Heat exchangers are most critical component. Slight political risk of changing water quality and environmental regulations. | 25
II.b | II.b.5.4 | TEA broninstallatie / rioolwarmtewisselaar (Thermische Energie uit Afvalwater) | Heat exchanger system capturing thermal energy from treated waste water (effluent). Includes filters, plate/tube heat exchanger, civil intake works and connecting pipework. | 30 | - | PlanEnergi/BPC (Engineering judgement) | 1 | N |  | Yes | 26.25 | 26.25 | 1 | 0 | Heat exchangers are most critical component. Slight political risk of changing water quality and environmental regulations. | 25
II.b.6 Heat Storage
II.b | II.b.6.1 | Large-scale hot water storage tank | Insulated steel pressure vessel or atmospheric tank for daily/weekly heat storage. Incl. tank, insulation, stratification systems and ancillary pipework. | 40 | 30-50 | ETC 0011 Ch. #141 | 0 | 0 | Tank vessel (~67% of cost) at 40yr dominates. | Yes | 27 | 27 | 0 | 0 | LOW risk on both axes. Proven long-life asset. | 27 |  |  |  | 30-50 | Technology Data Catalogue KEA BW (partly based on ETC)
II.b | II.b.6.2 | Pit Thermal Energy Storage (PTES) - short-mid-term or seasonal | Excavated pit with floating insulated cover for inter-seasonal heat storage. Incl. liner, top lid, stratification system and heat exchanger. | 30 | 25-35 | ETC 0011 Ch. #140 | 1 | 0 | Component analysis: top lid (20yr+) + pumps/controls (15yr) pull below ETC 30yr. | Yes | 25.8333 | 25.8333 | 1 | 0 | MEDIUM technical risk: Liner guaranteed performance for 20 yr, but being the critical component, the technical risk remains medium. LOW policy risk. | 20 |  |  |  | 20 | Technology Data Catalogue KEA BW (partly based on ETC) | For flexible use of PTES, shorter depreciation times should be considered, cf. the considerations regarding electric boilers depending on the design and expected application.
II.b | II.b.6.3 | ATES / WKO - Aquifer Thermal Energy Storage | Underground aquifer for seasonal heat/cold storage via injection and production wells. Incl. well infrastructure, HPs and surface equipment. | 30 | - | PlanEnergi/BPC (Engineering judgement) | 1 | 1 | Key split: well casings (~40yr), downhole pumps (~15yr), surface HP (15-25yr). | No | 0 | 30 | 1 | 0 | Little application in DK/ETC. Consolidated technology in NL. | 25
II.b.7 Auxiliary and Ancillary Systems
II.b | II.b.7.1 | Flue gas condensing unit | Condensing economiser recovering latent heat from boiler or CHP flue gas. Incl. stainless heat exchanger, condensate handling and controls. | 25 | - | PlanEnergi/BPC (Engineering judgement) | 1 | N | Corrosion-heavy environment. Condensation on heat exchanger. | No | 0 | 25 | 1 | 0 | MEDIUM technical risk: condensate environment accelerates degradation. Economic life 15yr. | 20
II.b | II.b.7.2 | Biomass fuel handling and storage system | Fuel reception, conveying, screening and storage for solid biomass. Incl. conveyors, silos, bunkers, dust extraction. | 25 | - | PlanEnergi/BPC (Engineering judgement) | 1 | N | Mechanical handling equipment (~40% of cost at 15-20yr) drives AMBER intensity. | No | 0 | 25 | 1 | 1 | MEDIUM risk of failure of critical components. Political risk follows considerations regarding use of biomass. | 20
II.b | II.b.7.3 | Electric boiler - Ancillary services | Eletric boiler used primarily for other primary goals than backup and peak production (e.g. anxillary services). Typically connected at mid-high voltage. | 20 | 20-25 | ETC 0018 Ch. #41 | 1 | 0 | Simple technology. Low equipment intensity. | Yes | 0 | 20 | 1 | 2 | High stranding risk, primarily due to risk of boundary conditions (electricity market changes). | 5 | [5 empty] | The technical design is broadly similar to electric boilers used for peak and backup heat production, and the unit may in practice also serve those purposes. The main differences are the grid connection level, typically higher voltage, and the operating profile, with rapid ramp-up, short-duration operation and participation in balancing services. Where the electric boiler is primarily installed for ancillary services, a shorter depreciation period is therefore appropriate, reflecting higher operational stress and greater exposure to market and regulatory changes.
II.c. Other Tangible Fixed Assets
II.c.1 Consumer / End-User Installations (DH-owned)
II.c | II.c.1.1 | HIU - single-family house (individuele afleverset, company-owned) | Compact delivery set connecting the DH network to a single-family house. Indirect connection incl. small Heat exchanger, thermostatic valve, heat meter connection and controls. In RAB only if the warmtebedrijf owns and maintains the HIU. | 25 | 20-30 | ETC 007 Ch. #203 (single family) | 2 | 0 | ETC 25yr too high per field experience. ETC Ch.07 #203: 25yr central, 20-30yr range for DH substation/HIU. | Yes | 18.8333 | 18.8333 | 2 | 1 | MEDIUM-HIGH technical risk: not overhauled; domestic environment. MEDIUM policy risk: individual HP competition. | 15 |  |  |  | 25 | Technology Data Catalogue KEA BW (partly based on ETC)
II.c | II.c.1.2 | HIU - multi-storey / commercial (individuele afleverset, company-owned) | Larger delivery set for multi-storey residential or commercial buildings. Indirect connection, incl. plate heat exchanger, pumps, thermostatic controls and heat meter. Better maintenance access than single-family. In RAB only if the warmtebedrijf owns and maintains the HIU. | 25 | 20-30 | ETC 007 Ch. #203 (apartment complex) | 2 | 0 | Better maintenance access than single-family. ETC Ch.07 #203: 25yr central, 20-30yr range. | Yes | 19.5 | 19.5 | 1 | 1 | MEDIUM technical risk: maintenance accessible; pumps replaceable. Same policy risk considerations as single-family HIU. | 20 |  |  |  | 25 | Technology Data Catalogue KEA BW (partly based on ETC)
II.c | II.c.1.3 | In-building distribution pipework (inpandig leidingstelsel, company-owned) | Collective riser and distribution pipework inside a (multi-unit) building, running between the central delivery connection at building entry and individual HIU connections at each apartment. In RAB only if the warmtebedrijf owns and has capitalised this infrastructure. Ownership varies significantly. | 45 | - | PlanEnergi/BPC (Engineering judgement) | 0 | 1 | The delivery boundary in Danish systems is outside or just inside the building, hence this is not a technology covered in ETC. However, the piping is the same as other and similar figures apply. | No | 0 | 45 | 0 | 1 | MEDIUM policy risk: building renovation cycles and DH customer churn. | 40
II.c | II.c.1.4 | Customer heat meters (company-owned) | Ultrasonic or mechanical heat meter at customer connection, owned and installed by the warmtebedrijf. Incl. flow sensor, temperature sensors and calculator. May be integrated in the HIU or be a separate unit (depending on ownership forms and delivery boundaries). In RAB only if the company owns the meters. | 15 | - | PlanEnergi/BPC (Engineering judgement) | 1 | N | Life driven by calibration requirements and electronic obsolescence. | No | 0 | 15 | 1 | 1 | Well-proven technology, stil being developed on. Change of versions of meters (in new connections etc.) may apply, posing a stranding risk of compatability between versions. | 15 |  | 5-10 | Fakturering efter faktisk förbrukning och reglering av mätperiodens längd avseende fjärrvärme, p. 41
II.c | II.c.1.5 | Individual booster heat pump (5th gen DHC - building level) | Small compression HP at building/apartment level boosting ambient loop (<=25 degC) to usable heating temperature. Typically 5-30 kW per unit. | 20 | 15-25 | ETC Ch.07 #207 (air-water HP, single - closest comparable) | 2 | 1 | No specific ETC DH entry. Comparable to 07 Ch. #207 air-water HP. Technical life 20 yr per Ch.07. | No | 0 | 20 | 2 | 1 | HIGH technical risk: factory unit, no overhaul in domestic context. MEDIUM policy risk: technology evolving rapidly. | 12
II.c.2 Vehicles and Mobile Equipment
II.c | II.c.2.1 | Service vehicles and mobile equipment | Service vehicles, lifting equipment and mobile test equipment for network O&M. | 10 | - | PlanEnergi/BPC (Engineering judgement) | 1 | N |  | No | 0 | 10 | 1 | 0 |  | 8
II.c.3 Other Fixed Assets
II.c | II.c.3.1 | ERP / operations management system (II.c variant) | Cross-reference I.1.1. Placement under II.c depends on ACM capitalisation policy. | 8 | - | PlanEnergi/BPC (Engineering judgement) | 2 | N | Life driven by vendor support cycles and functional obsolescence. | No | 0 | 8 | 1 | 0 | MEDIUM technical risk: IT hardware cycles. LOW policy risk. | 5
III. Third-Party Contributions
III | III.1 | Connection cost contribution (aansluitbijdrage / BAK) | One-off customer contribution towards DH connection costs. Reduces the net RAB; not itself depreciated. | - | - | Wcw / ACM methodology | N | N | Not a depreciable asset. | No | 0 |  | N | N | Not depreciable. | -
III | III.2 | Cost-covering contribution (kostendekkingsbijdrage) | Contributions from customers or third parties to cover part of the investment. Reduces the net RAB. | - | - | Wcw / ACM methodology | N | N | Not a depreciable asset. | No | 0 |  | N | N | Not depreciable. | -
III | III.3 | Subsidies, grants and other third-party contributions (WIS, SDE++, EU) | Government subsidies, EU grants or other public contributions received. Reduces the net Regulatory Asset Base (RAB). | - | - | Wcw / ACM methodology | N | N | Not a depreciable asset. | No | 0 |  | N | N | Not depreciable. | -
Note on H3: Asset Composition [0/1/2] - Step 1 Factor 1 0 = Low: structurally dominated; ETC reliable 1 = Medium: component split check recommended 2 = High: component analysis required N = N/A: not applicable
Note on I3: ETC Confidence - [0/1/2] - Step 1 Factor 1 0 = High: Primary ETC data (direct category match) 1 = Medium: Comparable ETC category or secondary source 2 = Low: Engineering judgment only (no ETC reference) N = N/A: Not applicable
Note on N3: Degradation Risk [0/1/2] -- Step 2 Factor 1 Risk of early wear and degradation, resulting in premature increase in O&M costs, compared to the corrected lifetime. 0 = Low: Stable O&M costs 1 = Medium: Moderate cost increase 2 = High: O&M cost escalation well before technical end of life
Note on O3: Policy / Stranding Risk [0/1/2] -- Step 2 Factor 2 Risk of early retirement due to policy, technology shift or demand loss 0 = Low: no foreseeable risk 1 = Medium: evolving technology or network risk 2 = High: clear phase-out
Note on T48: [Opmerkingenthread] U kunt deze opmerkingenthread lezen in uw versie van Excel. Eventuele wijzigingen aan de thread gaan echter verloren als het bestand wordt geopend in een nieuwere versie van Excel. Meer informatie: https://go.microsoft.com/fwlink/?linkid=870924 Opmerking: They have renovated them with change of kølemiddel and controls

## Component Assessment
Component Assessment
Read me: To edit the components of an asset category, either: a) override an existing component or b) override a "N/A"-blank To add new components, which have not been pre-filled: Go to the overview list in the bottom of the page (Line 552). This sheet is protected against editing (no password) in the lookup cells in columns D:E. If needed, remove the protection.
RAR Category | Sub-category (English) |  | Standard lifetime |  | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index |  | Notes
I. Intangible fixed assets | Research & development costs | ?
| Software | ?
| Other intangible fixed assets | ?
II.a Heat Networks | Transport Pipelines | Choose type | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation | Long-distance / high-temperature transmission network (WTB/HTO)
| Transport pipeline types | High pressure/high temp. forward >100 °C | 45 | PlanEnergi Engineering Judgement | 45 | 100 | 100 | 100%
| Average weighted lifetime Transport Pipelines | 45 | [5 empty] | 100%
| Primary Distribution Network | Choose type | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation | From heat source to neighbourhood distribution point
| Primary distribution pipeline types | Low pressure - medium temp. forward 65-85 °C | 45 | PlanEnergi Engineering Judgement | 45 | 100 | 100 | 100%
| Average weighted lifetime Primary Distribution Network | 45 | [5 empty] | 100%
| Secondary Distribution Network | Choose type | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation | From distribution point to local area
| Secondary distribution pipeline types | Low pressure - medium temp. forward 65-85 °C | 45 | PlanEnergi Engineering Judgement | 45 | 100 | 100 | 100%
| Average weighted lifetime Secondary Distribution Network | 45 | [5 empty] | 100%
| Branch Pipe for Consumer | Choose type | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation | From distribution pipe to customer real estate
| Branch pipe types | Low pressure - medium temp. PEX - Forward 65-85 °C | 35 | PlanEnergi Engineering Judgement | 35 | 100 | 100 | 100%
| Average weighted lifetime Branch Pipe for Consumer | 35 | [5 empty] | 100%
| Heat Transfer Station | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation | To transfer heat between Transport Pipeline, Primary distribution and secondary distribution.
| Plot of land | No | 0 | 0 | 0 | 0 | 0 | 0%
| Small building/enclosure for network station or power supply | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 7.823%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 9.126%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 100 | 5.476%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 18.25%
| Electrically controlled valves, regulation, shunts, on/off etc. | No | 0 | 0 | 0 | 0 | 0 | 0%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 9.126%
| Pressure control system | No | 0 | 0 | 0 | 0 | 0 | 0%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 18.25%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 18.25%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 13.69%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Transfer Station | 26.25 | [5 empty] | 100%
| Pump Station | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation | To boost pressure at long distances
| Plot of land | No | 0 | 0 | 0 | 0 | 0 | 0%
| Small building/enclosure for network station or power supply | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 9.569%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 100 | 6.699%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 22.33%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 22.33%
| Manually operated valves for service etc. | No | 0 | 0 | 0 | 0 | 0 | 0%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 22.33%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 16.75%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Pump Station | 25 | [5 empty] | 100%
II.b Production & Storage | Heat production plants | [7 empty] | Including boilers, biomass plants, geothermal, industrial waste heat
| Main Plant - Common Systems | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Plot of land | No | 0 | 0 | 0 | 0 | 0 | 0%
| Main building for overall heat plant | Yes | 50 | BPC Estimate | 50 | 100 | 500 | 25.64%
| High voltage power supply (transformers, switchboard, panels, meters etc.) | Yes | 25 | BPC Estimate | 25 | 100 | 50 | 5.128%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 50 | 6.41%
| Small building/enclosure for network station or power supply | No | 0 | 0 | 0 | 0 | 0 | 0%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 50 | 4.274%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 100 | 5.128%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 50 | 8.547%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 50 | 8.547%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 50 | 4.274%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 50 | 8.547%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 50 | 8.547%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 50 | 8.547%
| SCADA system | Yes | 20 | BPC Estimate | 20 | 100 | 50 | 6.41%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Main Plant - Common Systems | 36.3636 | [5 empty] | 100%
| Heat Production Unit 1: Air Source Heat Pump (Commercial Type HP) | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Commercial type HP - refrigeration system excluding water system, air coolers etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.53%
| Industrial type HP - refrigeration system excluding water system, air coolers etc. | No | 0 | 0 | 0 | 0 | 0 | 0%
| Cooling surfaces | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.53%
| Designated building for production unit | No | 0 | 0 | 0 | 0 | 0 | 0%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.263%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.579%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.53%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.53%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.263%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.53%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.53%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.53%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 7.895%
| High voltage power supply (transformers, switchboard, panels, meters etc.) | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 6.316%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 1: Air Source Heat Pump (Commercial Type HP) | 20.4348 | [5 empty] | 100%
| Heat Production Unit 2: Air Source Heat Pump (Industrial Type HP) | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Commercial type HP - refrigeration system excluding water system, air coolers etc. | No | 0 | 0 | 0 | 0 | 0 | 0%
| Industrial type HP - refrigeration system excluding water system, air coolers etc. | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 6.593%
| Cooling surfaces | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.99%
| Designated building for production unit | No | 0 | 0 | 0 | 0 | 0 | 0%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.495%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.648%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.99%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.99%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.495%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.99%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.99%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.99%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 8.242%
| High voltage power supply (transformers, switchboard, panels, meters etc.) | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 6.593%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 2: Air Source Heat Pump (Industrial Type HP) | 21.3043 | [5 empty] | 100%
| Heat Production Unit 3: Water/Water Heat Pump (Commercial Type HP) | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Commercial type HP - refrigeration system excluding water system, air coolers etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.318%
| Industrial type HP - refrigeration system excluding water system, air coolers etc. | No | 0 | 0 | 0 | 0 | 0 | 0%
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 3.993%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.659%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.398%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.318%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.318%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.659%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.318%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.318%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.318%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 6.988%
| High voltage power supply (transformers, switchboard, panels, meters etc.) | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 5.591%
| WKO Wells (casings) | Yes | 40 | BPC Estimate | 40 | 100 | 100 | 3.494%
| WKO Pumps (submerged) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.318%
| Small building/enclosure for network station or power supply | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 3.993%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 3: Water/Water Heat Pump (Commercial Type HP) | 23.7931 | [5 empty] | 100%
| Heat Production Unit 4: Water/Water Heat Pump (Industrial Type HP) | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Commercial type HP - refrigeration system excluding water system, air coolers etc. | No | 0 | 0 | 0 | 0 | 0 | 0%
| Industrial type HP - refrigeration system excluding water system, air coolers etc. | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.807%
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.148%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.839%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.452%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.679%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.679%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.839%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.679%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.679%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.679%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 7.259%
| High voltage power supply (transformers, switchboard, panels, meters etc.) | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 5.807%
| WKO Wells (casings) | Yes | 40 | BPC Estimate | 40 | 100 | 100 | 3.629%
| WKO Pumps (submerged) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.679%
| Small building/enclosure for network station or power supply | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.148%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 4: Water/Water Heat Pump (Industrial Type HP) | 24.4828 | [5 empty] | 100%
| Heat Production Unit 5: Waste Heat - Indirect Utilization | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 5.525%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 6.446%
| Cooling pipes and installation | Yes | 50 | Like DH-pipes | 50 | 100 | 50 | 1.934%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.89%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.89%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 6.446%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.89%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.89%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.89%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 9.669%
| Small building/enclosure for network station or power supply | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 5.525%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 5: Waste Heat - Indirect Utilization | 23.8095 | [5 empty] | 100%
| Heat Production Unit 6: Waste Heat - Direct Utilization | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 5.525%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 6.446%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.934%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.89%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.89%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 6.446%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.89%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.89%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.89%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 9.669%
| Small building/enclosure for network station or power supply | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 5.525%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 6: Waste Heat - Direct Utilization | 23.8095 | [5 empty] | 100%
| Heat Production Unit 7: Solar Heating Panels | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Plot of land | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| Solar heating panels | Yes | 30 | Energy Technology Catalogue | 30 | 100 | 100 | 5.551%
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.758%
| Small building/enclosure for network station or power supply | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.758%
| Glycol expansion system including tank | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 6.661%
| Glycol pipes and installation | Yes | 50 | Like DH-pipes | 50 | 100 | 50 | 1.665%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.551%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.665%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.1%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.1%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.551%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.1%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.1%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.1%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 8.327%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 7: Solar Heating Panels | 25.3846 | [5 empty] | 100%
| Heat Production Unit 8: TEO - Surface Water Heat Source | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.187%
| Small building/enclosure for network station or power supply | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.187%
| Water intake and outlet system (incl. diffusers and course filtering) | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.187%
| Back flush system for course filtering | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.77%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.885%
| Self-cleaning filtration system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.77%
| CIP-system for plate heat exchangers | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.77%
| Water and Glycol Pipes (low temp. Ambient loops) | Yes | 75 | PlanEnergi Engineering Judgement | 75 | 100 | 100 | 1.954%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.77%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.77%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.885%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.77%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.77%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 7.327%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 8: TEO - Surface Water Heat Source | 26.0714 | [5 empty] | 100%
| Heat Production Unit 9: TAO - Rinsed Sewage Water Heat Source | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.866%
| Small building/enclosure for network station or power supply | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.866%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.677%
| Self-cleaning filtration system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.35%
| CIP-system for plate heat exchangers | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.35%
| Water and Glycol Pipes (low temp. Ambient loops) | Yes | 75 | PlanEnergi Engineering Judgement | 75 | 100 | 100 | 2.271%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.35%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.35%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.677%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.35%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.35%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 8.516%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 9: TAO - Rinsed Sewage Water Heat Source | 26.25 | [5 empty] | 100%
| Heat Production Unit 10: Gas Turbine Combined Cycle | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 3.929%
| Turbines including combustion chamber, compressor and auxilliaries | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 3.929%
| Generator | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.501%
| Steam boiler including pumps, control system and auxilliaries | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 5.501%
| Condenser | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.501%
| High temperature HEX | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.501%
| Low temperature HEX | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.501%
| Chimney | Yes | 50 | BPC Estimate | 50 | 100 | 100 | 2.75%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.584%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.375%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.168%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.168%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.584%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.168%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.168%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.168%
| Power transformer | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 5.501%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 10: Gas Turbine Combined Cycle | 26.0606 | [5 empty] | 100%
| Heat Production Unit 11: Gas Engine | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.09%
| Engine including silencer, oil system etc. | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.726%
| Generator | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.726%
| High temperature HEX | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.726%
| Low temperature HEX | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.726%
| Condenser | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.726%
| Chimney | Yes | 50 | BPC Estimate | 50 | 100 | 100 | 2.863%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.772%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.431%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.543%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.543%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.772%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.543%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.543%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.543%
| Power transformer | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 5.726%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 11: Gas Engine | 25.4839 | [5 empty] | 100%
| Heat Production Unit 12: Electrical Boiler | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 5.51%
| Electrical boiler | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 7.713%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 6.428%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.928%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.86%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.86%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 6.428%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.86%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.86%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.86%
| High voltage power supply (transformers, switchboard, panels, meters etc.) | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 7.713%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 12: Electrical Boiler | 23.3333 | [5 empty] | 100%
| Heat Production Unit 13: Wood Chip Boiler | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.032%
| Furnace and boiler including feeding system, ash handling etc. | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.645%
| Electrostatic filter | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.645%
| Flue gas fan | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.645%
| Flue gas scrubbers | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.645%
| Absorption chiller | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.645%
| Chimney | Yes | 50 | BPC Estimate | 50 | 100 | 100 | 2.823%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.704%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.411%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.409%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.409%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.704%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.409%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.409%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 9.409%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 7.056%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 13: Wood Chip Boiler | 25.1613 | [5 empty] | 100%
| Heat Production Unit 14: Wood Chip CHP (ORC) | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 3.676%
| Furnace and boiler including feeding system, ash handling etc. | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.147%
| Electrostatic filter | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.147%
| Flue gas fan | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.147%
| Flue gas scrubbers | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.147%
| Chimney | Yes | 50 | BPC Estimate | 50 | 100 | 100 | 2.574%
| Steam turbine | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 3.676%
| ORC-system | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 5.147%
| Generator | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 5.147%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.289%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.287%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 8.578%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 8.578%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.289%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 8.578%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 8.578%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 8.578%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 6.434%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 14: Wood Chip CHP (ORC) | 25.7143 | [5 empty] | 100%
| Heat Production Unit 15: Wood Pellet Boiler | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 4.545%
| Furnace and boiler including feeding system, ash handling etc. | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 6.364%
| Flue gas filter | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 6.364%
| Flue gas fan | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 6.364%
| Chimney | Yes | 50 | BPC Estimate | 50 | 100 | 100 | 3.182%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.303%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.591%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.61%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.61%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.303%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.61%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.61%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 10.61%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 7.955%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Production Unit 15: Wood Pellet Boiler | 25.1852 | [5 empty] | 100%
| Heat Production Unit 16: Waste Incineration CHP | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 3.497%
| Furnace and boiler including feeding system, ash handling etc. | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 4.895%
| Flue gas filter | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 4.895%
| Flue gas fan | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 4.895%
| Flue gas scrubbers | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 4.895%
| Absorption chiller | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 4.895%
| Chimney | Yes | 50 | BPC Estimate | 50 | 100 | 100 | 2.448%
| Steam turbine | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 3.497%
| ORC-system | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 4.895%
| Generator | Yes | 25 | Energy Technology Catalogue | 25 | 100 | 100 | 4.895%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.079%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 50 | 1.224%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 8.159%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 8.159%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 4.079%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 8.159%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 8.159%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 8.159%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 6.119%
| Average weighted lifetime Heat Production Unit 16: Waste Incineration CHP | 25.6757 | [5 empty] | 100%
Heat storages
| Heat Storage Unit 1: Storage Tank | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Storage tank including insulation etc. | Yes | 40 | Energy Technology Catalogue | 40 | 100 | 100 | 11.35%
| Nitrogen system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 30.27%
| Small building/enclosure for network station or power supply | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 12.97%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 15.14%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 30.27%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Storage Unit 1: Storage Tank | 27 | [5 empty] | 100%
| Heat Storage Unit 2: Pit Thermal Energy Storage | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Plot of land | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| Pit (excavation) | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| Bottom liner | Yes | 30 | PlanEnergi Engineering Judgement | 30 | 100 | 100 | 6.13%
| Top lid | Yes | 20 | PlanEnergi Engineering Judgement | 20 | 100 | 100 | 9.194%
| Designated building for production unit | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 5.254%
| Small building/enclosure for network station or power supply | Yes | 35 | BPC Estimate | 35 | 100 | 100 | 5.254%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 6.13%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 100 | 3.678%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.26%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.26%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 6.13%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.26%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 12.26%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 9.194%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Storage Unit 2: Pit Thermal Energy Storage | 25.8333 | [5 empty] | 100%
| Heat Storage Unit 3: Aquifer Thermal Energy Storage (ATES) | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Plot of land | No | 0 | 0 | 0 | 0 | 0 | 0%
| WKO Wells (casings) | Yes | 40 | BPC Estimate | 40 | 100 | 100 | 4.354%
| WKO Pumps (submerged) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.61%
| Plate heat exchangers | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.806%
| DH Pipes and connections | Yes | 50 | BPC Estimate | 50 | 100 | 100 | 3.483%
| Circulation pumps including VSD's | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.61%
| Electrically controlled valves, regulation, shunts, on/off etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.61%
| Manually operated valves for service etc. | Yes | 30 | BPC Estimate | 30 | 100 | 100 | 5.806%
| Pressure control system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.61%
| Feed water/treatment system | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.61%
| Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 11.61%
| Low voltage power supply (switchboard, main panel, meter etc.) | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 8.708%
| Low pressure 5th gen. - Forward 25 °C | Yes | 80 | PlanEnergi Engineering Judgement | 80 | 100 | 100 | 2.177%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | No | 0 | 0 | 0 | 0 | 0 | 0%
| Average weighted lifetime Heat Storage Unit 3: Aquifer Thermal Energy Storage (ATES) | 28.3333 | [5 empty] | 100%
II.c Other fixed assets | End User Installations – Single Family House | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Internal piping system (in-building) | No | 0 | 0 | 0 | 0 | 0 | 0% | Pipes inside the customer's building, where owned by the DH company
| Standard DH Delivery set / heat interface unit for single family houses | Yes | 18 | BPC Estimate | 18 | 100 | 100 | 16.89% | The customer-side heat exchanger unit, life time and depreciation is similar to direct heat exchanger, indirect heat exchanger, direct tank and indirect tank.
| Standard DH Delivery set / heat interface unit for multi storey buildings/industries | No | 0 | 0 | 0 | 0 | 0 | 0%
| Heat meter | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 15.2%
| Smart meter communication module | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 20.27%
| DHW Tank | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 15.2%
| 5th gen. Power supply for heat pump and temperature boosting | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 12.16%
| 5th gen. Heat pump | No | 0 | 0 | 0 | 0 | 0 | 0%
| 5th gen. Circulation pump, shuntvalve etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 20.27%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0% | Residual category
| Average weighted lifetime End User Installations – Single Family House | 18.8333 | [5 empty] | 100%
| End User Installations – Multi-Storey House | Is component included? (Yes or No) | Standard lifetime | Standard lifetime reference | Corrected lifetime (if needed) | Standard cost allocation index | Corrected cost allocation index | Annual %-cost allocation
| Internal piping system (in-building) | No | 0 | 0 | 0 | 0 | 0 | 0% | Pipes inside the customer's building, where owned by the DH company
| Standard DH Delivery set / heat interface unit for single family houses | No | 0 | 0 | 0 | 0 | 0 | 0% | The customer-side heat exchanger unit, life time and depreciation is similar to direct heat exchanger, indirect heat exchanger, direct tank and indirect tank.
| Standard DH Delivery set / heat interface unit for multi storey buildings/industries | Yes | 22 | BPC Estimate | 22 | 100 | 100 | 14.26%
| Heat meter | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 15.68%
| Smart meter communication module | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 20.91%
| DHW Tank | Yes | 20 | BPC Estimate | 20 | 100 | 100 | 15.68%
| 5th gen. Power supply for heat pump and temperature boosting | Yes | 25 | BPC Estimate | 25 | 100 | 100 | 12.55%
| 5th gen. Heat pump | No | 0 | 0 | 0 | 0 | 0 | 0%
| 5th gen. Circulation pump, shuntvalve etc. | Yes | 15 | BPC Estimate | 15 | 100 | 100 | 20.91%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0%
| N/A | Yes | 0 | 0 | 0 | 0 | 0 | 0% | Residual category
| Average weighted lifetime End User Installations – Multi-Storey House | 19.5 | [5 empty] | 100%
Data input - component level | Change standard parameters
|  |  | Standard lifetime |  | Lifetime reference |  |  |  | Same lifetime in Germany & Sweden | Notes on Lifetime
| Networks | High pressure/high temp. forward >100 °C | 45 |  | PlanEnergi Engineering Judgement |  |  |  | ?
|  | Low pressure - medium temp. forward 65-85 °C | 45 |  | PlanEnergi Engineering Judgement |  |  |  | ?
|  | Low pressure - medium temp. PEX - Forward 65-85 °C | 35 |  | PlanEnergi Engineering Judgement |  |  |  | ?
|  | Low pressure 5th gen. - Forward 25 °C | 80 |  | PlanEnergi Engineering Judgement |  |  |  | ?
|  | Water and Glycol Pipes (low temp. Ambient loops) | 75 |  | PlanEnergi Engineering Judgement
|  | None | 0
[5 empty] | Lifetime reference |  |  |  | Same lifetime in Germany & Sweden | Notes on Lifetime
| Buildings | Plot of land | 0 | [5 empty] | Yes
|  | Small building/enclosure for network station or power supply | 35 |  | BPC Estimate |  |  |  | Yes - same types are used | Could be longer dependent on type
|  | Main building for overall heat plant | 50 |  | BPC Estimate |  |  |  | Yes - same types are used | Could be longer dependent on type
|  | Designated building for production unit | 35 |  | BPC Estimate |  |  |  | Yes - same types are used | Could be longer dependent on type
[5 empty] | Lifetime reference |  |  |  | Same lifetime in Germany & Sweden | Notes on Lifetime
| General | Plate heat exchangers | 30 |  | BPC Estimate |  |  |  | Yes - same types are used
|  | DH Pipes and connections | 50 |  | BPC Estimate |  |  |  | Yes
|  | Circulation pumps including VSD's | 15 |  | BPC Estimate |  |  |  | Yes - same types are used
|  | Electrically controlled valves, regulation, shunts, on/off etc. | 15 |  | BPC Estimate |  |  |  | Yes - same types are used
|  | Manually operated valves for service etc. | 30 |  | BPC Estimate |  |  |  | Yes - same types are used
|  | Pressure control system | 15 |  | BPC Estimate |  |  |  | ?
|  | Feed water/treatment system | 15 |  | BPC Estimate |  |  |  | ?
|  | Control system (Transmitters, Panels, PLC's, communication to SCADA etc.) | 15 |  | BPC Estimate |  |  |  | Yes - same types are used
|  | IT-equipment, LAN, cameras etc. | 7 |  | BPC Estimate |  |  |  | Yes - same types are used
|  | SCADA system | 20 |  | BPC Estimate |  |  |  | ?
[5 empty] | Lifetime reference |  |  |  | Same lifetime in Germany & Sweden | Notes on Lifetime
| Power supply | Low voltage power supply (switchboard, main panel, meter etc.) | 20 |  | BPC Estimate |  |  |  | Yes - same types are used
|  | High voltage power supply (transformers, switchboard, panels, meters etc.) | 25 |  | BPC Estimate |  |  |  | Yes - same types are used
[5 empty] | Lifetime reference |  |  |  | Same lifetime in Germany & Sweden | Notes on Lifetime
| Heat production | Commercial type HP - refrigeration system excluding water system, air coolers etc. | 15 |  | BPC Estimate |  |  |  | Could be other types but lifetime should be similar | No overhauls or replacement of wearing parts
|  | Cooling surfaces | 15 |  | BPC Estimate |  |  |  | Yes - same types are used
|  | Industrial type HP - refrigeration system excluding water system, air coolers etc. | 25 |  | Energy Technology Catalogue |  |  |  | Could be even longer as they use very large components | Overhauls and replacement of wearing parts
|  | Cooling pipes and installation | 50 |  | Like DH-pipes |  |  |  | ? | Could be plastic, which has longer life with low temps
Waste heat - direct utilization
Waste heat - indirect utilization
Gas-/oil boiler
|  | Burner | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Boiler | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
Gas engine
|  | Engine including silencer, oil system etc. | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Generator | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | High temperature HEX | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Low temperature HEX | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Condenser | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Chimney | 50 |  | BPC Estimate |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
Gas turbine
|  | Turbines including combustion chamber, compressor and auxilliaries | 35 |  | BPC Estimate |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Steam boiler including pumps, control system and auxilliaries | 25 |  | BPC Estimate |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Power transformer | 25 |  | BPC Estimate |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Electrical boiler | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Solar heating panels | 30 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Glycol expansion system including tank | 25 |  | BPC Estimate |  |  |  | ? | Same as cooling pipes
|  | Glycol pipes and installation | 50 |  | Like DH-pipes |  |  |  | ?
TEO - Surface Water Intake
|  | Water intake and outlet system (incl. diffusers and course filtering) | 35 |  | BPC Estimate
|  | Back flush system for course filtering | 15 |  | BPC Estimate
|  | Self-cleaning filtration system | 15 |  | BPC Estimate
|  | CIP-system for plate heat exchangers | 15 |  | BPC Estimate
|  | Wood chip boiler | 25 |  | Energy Technology Catalogue |  |  |  | ? | Technology Catalogue consider entire unit as one component
|  | Steam turbine | 35 |  | BPC Estimate |  |  |  | Yes - same types are used | Gas turbines in Hillerød, Silkeborg og Viborg >30 år. Viborg og Hillerød kunne være forlænget yderligere.
|  | ORC-system | 25 |  | BPC Estimate |  |  |  | Yes - same types are used | Similar to industrial heat pumps. Internet A/I search confirm 25 yrs.
|  | Furnace and boiler including feeding system, ash handling etc. | 25 |  | Energy Technology Catalogue |  |  |  | ? | Technology Catalogue consider entire unit as one component
|  | Electrostatic filter | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Flue gas fan | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Flue gas scrubbers | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Absorption chiller | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | 2020-version of Tech Cat.
|  | Wood chip CHP | 25 |  | Energy Technology Catalogue |  |  |  | ? | Technology Catalogue consider entire unit as one component
|  | Wood pellet boiler | 25 |  | Energy Technology Catalogue |  |  |  | ? | Technology Catalogue consider entire unit as one component
|  | Flue gas filter | 25 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Waste incineration | 25 |  | Energy Technology Catalogue |  |  |  | ? | Technology Catalogue consider entire unit as one component
|  | Waste incineration CHP | 25 |  | Energy Technology Catalogue |  |  |  | ? | Technology Catalogue consider entire unit as one component
Notes on Lifetime
| Storages | Storage tank including insulation etc. | 40 |  | Energy Technology Catalogue |  |  |  | Yes - same types are used | Technology Catalogue consider entire unit as one component
|  | Nitrogen system | 15 |  | BPC Estimate |  |  |  | ?
|  | Pit (excavation) | 0 | [5 empty] | Yes
|  | Bottom liner | 30 |  | PlanEnergi Engineering Judgement |  |  |  | Yes - same types are used (according to Geoffrey but depends on construction company)
|  | Top lid | 20 |  | PlanEnergi Engineering Judgement |  |  |  | Yes - same types are used (according to Geoffrey but depends on construction company)
|  | WKO Wells (casings) | 40 |  | BPC Estimate |  |  |  | ? - could differ as soil is different (limestone in Denmark) | Internet research
|  | WKO Pumps (submerged) | 15 |  | BPC Estimate |  |  |  | ? - could differ as soil is different (limestone in Denmark) | Internet research
Notes on Lifetime
| End users | Internal piping system (in-building) | 50 |  | Same as DH |  |  |  | Should be similar
|  | Standard DH Delivery set / heat interface unit for single family houses | 18 |  | BPC Estimate |  |  |  | ? | Technology Catalogue. says 25 but seems too high (15 years more likely)
|  | Standard DH Delivery set / heat interface unit for multi storey buildings/industries | 22 |  | BPC Estimate |  |  |  | ? | Technology Catalogue. says 25 but seems too high (15 years more likely)
|  | Heat meter | 20 |  | BPC Estimate |  |  |  | ?
|  | Smart meter communication module | 15 |  | BPC Estimate |  |  |  | ? | Could be technical obsolete in shorter time
|  | DHW Tank | 20 |  | BPC Estimate |  |  |  | ?
|  | 5th gen. Power supply for heat pump and temperature boosting | 25 |  | BPC Estimate |  |  |  | Should be similar
|  | 5th gen. Heat pump | 15 |  | BPC Estimate |  |  |  | Probably a niche product in most countries | Technology Catalogue says 25 but seems too high
|  | 5th gen. Circulation pump, shuntvalve etc. | 15 |  | BPC Estimate |  |  |  | Should be similar
Lookup and datalists
List 1 | ID | Technological asset list | Overview of weighted lifetimes |  |  | Years
Yes | II.a.1.1 | Transmission pipes | Average weighted lifetime Transport Pipelines |  |  | 45
No | II.a.1.2 | Primary distribution pipes | Average weighted lifetime Primary Distribution Network |  |  | 45
| II.a.1.3 | Secondary distribution pipes | Average weighted lifetime Secondary Distribution Network |  |  | 45
| II.a.1.4 | Service connections / house connections | Average weighted lifetime Branch Pipe for Consumer |  |  | 35
| II.a.2.1 | Area-level heat transfer station / substation | Average weighted lifetime Heat Transfer Station |  |  | 26.25
| II.a.3.1 | Main network circulation pumping station | Average weighted lifetime Pump Station |  |  | 25
| II.a.6.2 | Operations and Administration Building | Average weighted lifetime Main Plant - Common Systems |  |  | 36.3636
| II.b.3.1a | A/W HP - commercial type (<=5 MW, factory unit) | Average weighted lifetime Heat Production Unit 1: Air Source Heat Pump (Commercial Type HP) |  |  | 20.4348
| II.b.3.1b | A/W HP - industrial type (>5 MW) | Average weighted lifetime Heat Production Unit 2: Air Source Heat Pump (Industrial Type HP) |  |  | 21.3043
| II.b.3.2a | W/W HP - commercial type | Average weighted lifetime Heat Production Unit 3: Water/Water Heat Pump (Commercial Type HP) |  |  | 23.7931
| II.b.3.2b | W/W HP - industrial type | Average weighted lifetime Heat Production Unit 4: Water/Water Heat Pump (Industrial Type HP) |  |  | 24.4828
| II.b.5.2 | Waste heat recovery installation | Average weighted lifetime Heat Production Unit 5: Waste Heat - Indirect Utilization |  |  | 23.8095
| II.b.5.2 | Waste heat recovery installation | Average weighted lifetime Heat Production Unit 6: Waste Heat - Direct Utilization |  |  | 23.8095
| II.b.5.1 | Solar district heating - collector field | Average weighted lifetime Heat Production Unit 7: Solar Heating Panels |  |  | 25.3846
| II.b.5.3 | TEO broninstallatie (Thermische Energie uit Oppervlaktewater) | Average weighted lifetime Heat Production Unit 8: TEO - Surface Water Heat Source |  |  | 26.0714
| II.b.5.4 | TEA broninstallatie / rioolwarmtewisselaar (Thermische Energie uit Afvalwater) | Average weighted lifetime Heat Production Unit 9: TAO - Rinsed Sewage Water Heat Source |  |  | 26.25
| II.b.2.2 | Gas turbine Combined Cycle | Average weighted lifetime Heat Production Unit 10: Gas Turbine Combined Cycle |  |  | 26.0606
| II.b.2.1 | Gas engine CHP | Average weighted lifetime Heat Production Unit 11: Gas Engine |  |  | 25.4839
| II.b.1.2 | Electric boiler - peak / backup | Average weighted lifetime Heat Production Unit 12: Electrical Boiler |  |  | 23.3333
| II.b.1.3 | Wood chip boiler - standalone production unit | Average weighted lifetime Heat Production Unit 13: Wood Chip Boiler |  |  | 25.1613
| II.b.2.4 | Biomass CHP (wood chips / pellets / straw) | Average weighted lifetime Heat Production Unit 14: Wood Chip CHP (ORC) |  |  | 25.7143
| II.b.1.3 | Wood chip boiler - standalone production unit | Average weighted lifetime Heat Production Unit 15: Wood Pellet Boiler |  |  | 25.1852
| II.b.2.3 | Waste-to-Energy (WtE) CHP | Average weighted lifetime Heat Production Unit 16: Waste Incineration CHP |  |  | 25.6757
| II.b.6.1 | Large-scale hot water storage tank | Average weighted lifetime Heat Storage Unit 1: Storage Tank |  |  | 27
| II.b.6.2 | Pit Thermal Energy Storage (PTES) - short-mid-term or seasonal | Average weighted lifetime Heat Storage Unit 2: Pit Thermal Energy Storage |  |  | 25.8333
| II.b.6.3 | ATES / WKO - Aquifer Thermal Energy Storage | Average weighted lifetime Heat Storage Unit 3: Aquifer Thermal Energy Storage (ATES) |  |  | 28.3333
| II.c.1.1 | HIU - single-family house (individuele afleverset, company-owned) | Average weighted lifetime End User Installations – Single Family House |  |  | 18.8333
| II.c.1.2 | HIU - multi-storey / commercial (individuele afleverset, company-owned) | Average weighted lifetime End User Installations – Multi-Storey House |  |  | 19.5

## Wcw Definitions
Warmtewet collectief (Wcw) Art. 1.1 — Key definitions for Asset Assessment
Dutch term (Wcw) | English translation | Wcw definition (summary) | Project context / relevance | In RAB? | Asset list ref.
Network layers
warmtenet | District heating network | All interconnected pipes, equipment and installations for heat transport to/from consumers and producers. Explicitly excludes: inpandig leidingstelsel, binneninstallatie, afleversets. | Primary asset base of the warmtebedrijf. Most RAB assets sit here: distribution pipes, substations, pumping stations, valves, metering, civil works. | Yes | II.a.*
warmtetransportnet | Heat transport network | Regional-level transmission grid connecting heat sources to collective distribution systems or large off-takers. Separate legal regime from the warmtenet. | The WTB / HTO layer. Separate regulatory section; assessed on HTO sheet. | Yes (HTO) | HTO sheet
warmtebedrijf | Heat company | Entity responsible for heat transport, delivery and supply. Excludes landlords and VvEs that merely re-sell heat (doorlevering). | The primary regulated entity whose RAB is assessed in Phase 1. | N/A | —
Customer boundary assets
afleverset voor warmte | Delivery set / Heat interface unit (HIU) | Heat transfer unit at the customer boundary. Two variants: individuele (between warmtenet or inpandig leidingstelsel and binneninstallatie) and collectieve (between warmtenet and inpandig leidingstelsel in a multi-unit building). Excluded from warmtenet and binneninstallatie. | Key survey discrepancy: ownership determines RAB inclusion. Appears in both II.a.2.2 (II.a classification) and II.c.1.1/II.c.1.2 (II.c, company-owned). | If company-owned | II.a.2.2, II.c.1.1, II.c.1.2
individuele afleverset | Individual delivery set / HIU | Delivery set transferring heat between warmtenet (or inpandig leidingstelsel) and a single property's binneninstallatie. One unit per apartment or house. | Single-family: II.c.1.1. Multi-storey per apartment: II.c.1.2. Also referenced under II.a.2.2 for companies classifying under II.a. | If company-owned | II.c.1.1, II.c.1.2, II.a.2.2
collectieve afleverset | Collective delivery set / building-level HIU | Delivery set transferring heat between the warmtenet and the inpandig leidingstelsel — the unit serving the whole building at building entry. | Building-level substation. More consistently company-owned. → II.a.2.1. | Yes (typically) | II.a.2.1
inpandig leidingstelsel | In-building distribution system / collective riser | Collective riser pipework inside a building between the central connection at building entry and individual apartment connections. Excluded from warmtenet by definition. | In RAB only if company-owned. Ownership varies significantly — confirm per company. VvE/customer-owned → not in RAB. | If company-owned | II.c.1.3
binneninstallatie | Internal (customer) installation | Pipes and equipment inside a property for that property's heating/hot water needs. Excludes afleverset, warmtemeter, and pipes to other properties. | Customer-owned. Not in RAB. The radiator, underfloor heating circuit, domestic hot water. | No | —
Connections
individuele leveringsaansluiting | Individual supply connection / house connection | Pipe(s) from warmtenet or inpandig leidingstelsel to the individual delivery set. Bounded by shut-off valve (building side) and network branch (network side). | The 'house connection' or 'service pipe'. Company-owned. | Yes | II.a.1.4
centrale leveringsaansluiting | Central supply connection / building entry connection | Pipe(s) between warmtenet and the inpandig leidingstelsel at a multi-unit building. | Building-level entry connection. Part of the warmtenet asset base. | Yes | II.a.1.*
Metering
warmtemeter | Heat meter | Device measuring delivered heat. Defined by EU MID Directive Annex III. Excluded from both warmtenet and binneninstallatie. Subject to MID certification (Metrologiewet NL). | In RAB only if company-owned. Key survey discrepancy. See II.a.5.1 (company-owned customer meter) and II.c.4.8 (component reference). | If company-owned | II.a.5.1, II.c.4.8
Other relevant terms
warmtebron | Heat source | Installation where thermal energy is generated or released. | Heat production assets: boilers, heat pumps, geothermal, CHP. See II.b. | Yes | II.b.*
doorlevering van warmte | Re-delivery / resale of heat | Heat delivered by a landlord to tenants or VvE to members, purchased from the warmtebedrijf. These parties are excluded from the warmtebedrijf definition. | VvE and housing corporations reselling heat are not regulated as warmtebedrijven. Their in-building assets are not in the RAB of the warmtebedrijf. | N/A | Boundary note
economische eigendom | Economic ownership | Bundle of rights representing an interest in an asset (incl. value-change risk), held by a party other than the legal owner. | Relevant for HIUs and meters financed off-balance-sheet. Economic ownership determines RAB inclusion even if legal title lies elsewhere. | N/A | Ownership note